## page 1
Status Message | Status Message Description | Turbine State | Brake Procedure | Impact on Operation | Reset | Error Identification
1 | Program start PLC | AF Down Time | 2 | OK | L/R | Turbine controller was freshly started, automatic reset is only executed after a grid outage
2 | No Errors | OK OK Time | 0 | OK | A | Turbine free of error
3 | Manual Stop | OK OK Time | 2 | TRIP | A | Manual stop from switching box key or turbine Web Page (general control function)
6 | System OK | OK OK Time | 0 | OK | A | No error and no manual stop
7 | Storm shutdown | WE Weather Outage Time | 2 | TRIP | A/L/R | Wind P6.5 (P_StormShutdownWindSpd) time averaged P6.6 (P_StormShutdownTime) exceeded or Wind P6.7 (P_StormGustWindSpd) exceeded for period P6.8 (P_StormGustTime) or in full load operation, blade angle exceeded P12.11(P_BladeAngleInLoadMax) for a period P6.8(P_StormGustTime) or 10 min. averaged wind speed exceeds P6.11 (P_StormShutdownWindSpd10Min) or Averaged gen. Speed > P2.2
8 | Overvoltage | NA Grid | 14 | TRIP | A/L/R | One line voltage exceeded P20.1 (P_LineVoltageMax) for a period P20.7 (P_LineVoltageReactionTimeMax) BP depending on brake type and then BP 6
9 | Undervoltage | NA Grid | 14 | TRIP | A/L/R | One of the line voltages below P20.2(P_LineVoltageMin) for a period P20.8(P_LineVoltageReactionTimeMin) Or one of the line voltages below LVRT characteristic for 150msec, BP depending on brake type and then BP 6
10 | Underfrequency | Line Out Time | 14 | TRIP | A | Only for NGG: The Converter is reporting grid underfrequency (DI_In_CuGridUnderFreqFault)
11 | Overfrequency | Line Out Time | 14 | TRIP | A | Only for NGG: The Converter is reporting grid overfrequency (DI_In_CuGridOverFreqFault)
13 | Asymmetric |  | 14 | TRIP | L/R | 2 current phased deviate from one another by P20.5 (P_PhaseCurrentAsymmetry) for more than 5 s
14 | Generator | AF Down | 14 | TRIP | L/R | Generator speed exceeded P1.1 (P_GenSpdMax), for a period of P1.2 (P_GenOverSpdPeriod), either speed calculated by CCU or turbine controller
15 | Rotor overspeed | AF Down | 14 | TRIP | L/R | Rotor speed exceeded P1.3 (P_RotSpdMax) for a period of P1.4 (P_RotOverSpdPeriod)
16 | Rotor Monitor | AF Down | 6.3 | TRIP | L/R | Overspeed on (rotor) monitor. Proximity switch between gearbox and generator
19 | Maximum motor | AF Down | 14 | TRIP | L/R | Power drops below P4.10 (P_MotorPowerMax) for 1 sec
20 |  | OK OK Time | 2 | TRIP | A/L/R | P11.5 (P_YawCableTwistStopRevs)
21 | Cable twisting left | OK OK Time | 2 | TRIP | A/L/R | P11.5 (P_YawCableTwistStopRevs) nacelle rotations in idling state or P11.6 (P_YawCableTwistUnwindingRevs) rotations in all states exceeded
22 | Yaw position at maximum turns | AF Down | 2 | TRIP | L/R | Nacelle rotations P11.7 (P_YawCableTwistEndingRevs) exceeded
23 | Time over power | AF Down | 14 | TRIP | A/L/R | Power threshold exceeded for a period. Threshold and period are set dependent on: P4.2(P_GenPeakPower) P4.3(P_GenPeakPowerTime) With activated Wind Inertia (WI) feature
24 | Primary pitch braking time too long | AF Down Time | 6.2 | TRIP | L/R | Blade drive time P8.7 for type 2 braking to feathered pitch position
25 | Primary Pitch braking not effective | AF Down Time | 6.2 | TRIP | L/R | No reduction in generator speed with braking procedures 3, 4, or 5 after 3 seconds (monitored for every 1.4 sec). Only monitored when rotor speed > 300 rpm.
27 | Secondary hydraulic braking time too long | AF Down Time | 6.2* | TRIP | L/R | Not below speed of 80 rpm after a period P8.6 (P_SecBrakingTime) after application of brake. During secondary brake test a period of 1.5 * P8.6 (P_SecBrakingTime) is taken.
28 | Secondary hydraulic braking not effective | AF Down Time | 6.2* | TRIP | L/R | No reduction in generator speed with braking procedures 6 or 7 after 3 seconds (monitored for every 1.4 sec). Only monitored when generator speed > 300 rpm
31 | Fault yaw counter system | AF Down Time | 2 | TRIP | L/R | Yaw encoding system malfunction as proximity sensor 1 and 2 fault
34 | Secondary hydraulic brake not released | AF Down Time | 14 | TRIP | L/R | After period P9.6 (P_BrakeReleaseDelayTime) following opening of the passive brake, the brake is not released for a period of P9.9(P_BrakeReleaseTime), After period P9.6(P_BrakeReleaseDelayTime) following opening of the active brake, the brake is not released for a period of P9.9(P_BrakeReleaseTime), resp.
35 | Emergency stop downtower | AF Down Time | 6.3 | TRIP | L/R | Emergency off button activated in control box
36 | Holding speed exceeded with brakes applied | AF Down Time | 6.3 | TRIP | L/R | Gen. Speed exceeded 14 rpm / rotor speed 1.5 rpm 30 sec after application of brake
38 | Secondary brake test | OK OK Time | 7 | OK | A/L/R | Brake test after 1400 h below power 500 kW without pitching the rotor blades
41 | Tower vibration sensor failure | AF Down Time | 2 | TRIP | L/R | Monitoring tower accelerometer in four different ways: 1. While brake proc. 3-6 Acceleration is not exceeding testlevel(P7.11(P_TwrVibrationMeaAccel Thrsh)) 2. Self test Start cond.: every 24h, feathered position and acceleration < (P7.11 (P_TwrVibrationMeaAccelThrsh))/2): Test
42 | Yawing in wrong direction | AF Down | 2 | TRIP | A/L/R | Detection of wrong direction: nacelle is turning in another direction as yaw motor direction, reaction: apply yaw brakes immediately. And reset timer / counter for wind direction tracking. Number of reaction: Occurrences: 1. No fault message, no shut down, 2. Shut down turbine with SM 42, 3. In feathered pos. at v = v3: restart locked, yaw drive locked for v>v3-5m/s, 4. In feathered pos. at v<v3-5m/s SM42
45 | Hydraulic pump | AF Down | 2 | TRIP | L/R | Hydraulic pump period above P9.5 (P_PumpOnTimeMax)(no pressure built up in the period) AND brake failure derating function disabled by command
46 | Hydraulic pump | AF Down | 2 | TRIP | A/L/R | Hydraulic pump interval period below P9.4 (P_PumpIntervalTimeMin) six times in a row AND brake fault de-rating function disabled by command
47 | Service switch | WA | 2 | TRIP | L/R | Hydraulic service switch activated
48 | Hydraulic oil level low | AF Down | 2 | TRIP | L/R | SM_In_HydrOilLevelLow is set to 0 in 1.6-100m wind turbine.
51 | Gearbox oil level too low | AF Down | 2 | TRIP | A/L/R | 1. Oil low event detected by: The oil level of the gearbox is too low for the time P10.2 (P_GbxOilLevelLowTime). The monitoring begins if the oil temperature is above P10.13 (P_GbxMonOilLevelOilTempMin), but not below 5°C. 2, P43.13 (P_GbxExtendOPtime) passed since the event happen
52 | Gearbox oil | AF Down | 2 | TRIP | L/R | Gearbox oil pressure too low for a period P10.1 (P_GbxOilPressureLowTime) delayed for a period P10.8 (P_GbxOilPressureMonDelayTime) after switching on pump
53 | Wind vane failure | AF Down | 2 | TRIP | A/L/R | Yaw adjustment angle 200° exceeded and no change in center signal Additional monitor for NRG wind vane (P26.3 Bit4 (P_NRGTypeWindVaneEnable) =1): both center signals (yaw right/left error,) are low for 10 sec, or both center signals are high permanently and high wind for 600 sec (>4-5m/s)
54 | Anemometer | AF Down | 2 | TRIP | A/L/R | Power P6.9 (P_AnemometerMonPower) exceeded for period P6.10 (P_AnemometerDelayMonitorTime) and wind less than 4 m/s for period P6.10 (P_AnemometerDelayMonitorTime)
55 | Rotor speed | AF Down | 2 | TRIP | L/R | No rotor pulses for 10 sec, if generator speed above P1.11 (P_GenSpdMonMin)
56 | Generator speed | AF Down | 2 | TRIP | L/R | No generator pulses for 10 sec, if rotor speed above P1.11 (P_GenSpdMonMin)/P1.5 (P_GenRotSpdRatio)
57 | Incorrect | AF Down | 14 | TRIP | L/R | Deviation P1.6 (P_SpdDevMax) generator /rotor speed for period P1.7 (P_SpdDevPeriod). Exceeded and (generator speed exceeds P1.11 (P_GenSpdMonMin) or rotor speed exceeds P1.11 (P_GenSpdMonMin)/ P1.5 (P_GenRotSpdRatio)
58 | Demand to stop by an external device | EX External | 2 | TRIP | A | External command (Energy curtailment)
59 | Tower Vibration |  | 6.3 | TRIP | L/R | Vibration switch activated
60 | Yaw limit switch activated | AF Down | 2 | TRIP | L/R | Yaw limit switch activated
63 | Safety chain | AF Down | 6.3 | TRIP | L/R | Safety chain activated
65 | Main switch | AF Down | 14 | TRIP | L/R | Power switch activated
71 | Gearbox oil filter (alarm) | AF Down | 2 | TRIP | SC | Filter soiled (coarse) for period P10.6 (P_GbxFilterTime) or For combi filter SM89 is active for period P8.15 (P_GbxSoiledOilFilterDlyTime)
72 | Gearbox oil over temperature from thermal switch | AF Down | 2 | TRIP | L/R | Input gearbox overtemp for 60 sec
75 | Generator bearing A over temperature | AF Down Time | 2 | TRIP | A/L/R | Generator bearing temperature counter Xn >= P36.11 (P_GenTriggerValueTrigAlg) or generator bearing temperature > P36.13 (P_GenEndValueTrigAlg) for a time period of 10 sec. Generator bearing temperature counter Xn algorithm: - In temperature range P36.12 (P_GenTransitionValueTrigAlg) to P36.13 (P_GenEndValueTrigAlg): Xn=Xn-1 + P36.9 (P_GenCurveCharactTrigAlg)/(P36.10 (P_GenAsymptoteTrigAlg) -TBRG)³ - In temperature range < P36.12: Xn=Xn-1 – (P36.11 (P_GenTriggerValueTrigAlg)/(P36.14 (P_GenDecrTimeTrigAlg) – 3600)) Algorithm will result in a shutdown at: - Generator bearing temperature > P36.13 (P_GenEndValueTrigAlg) or - Generator bearing temperature > P36.12 (P_GenTransitionValueTrigAlg) for 12h Restart: Generator bearing temperature < P36.12 (P_ShaftBearingTempMax) -15°C and generator bearing temperature counter Xn < 36.11 (P_GenTriggerValueTrigAlg)
76 | Generator bearing B over temperature | AF Down Time | 2 | TRIP | A/L/R | Generator bearing temperature counter Xn >= P36.11 (P_GenTriggerValueTrigAlg) or generator bearing temperature > P36.13 (P_GenEndValueTrigAlg) for a time period of 10 sec. Generator bearing temperature counter Xn algorithm: - In temperature range P36.12 (P_GenTransitionValueTrigAlg) to P36.13 (P_GenEndValueTrigAlg): Xn=Xn-1+ P36.9 (P_GenCurveCharactTrigAlg)/(P36.10 (P_GenAsymptoteTrigAlg) -TBRG)³ - In temperature range < P36.12: Xn=Xn-1 – (P36.11 (P_GenTriggerValueTrigAlg)/(P36.14 (P_GenDecrTimeTrigAlg) – 3600)) Algorithm will result in a shutdown at: - Generator bearing temperature > P36.13 (P_GenEndValueTrigAlg) or - Generator bearing temperature > P36.12 (P_ShaftBearingTempMax) for 12h Restart: Generator bearing
77 | Gearbox oil over temperature | AF Down Time | 2 | TRIP | A/L/R | Temperature above P13.8 (P_GbxOilTempMax) for 60 sec, restart: Temperature under P13.8 (P_GbxOilTempMax) – 15°C
78 | Outside temperature too low | WE Weather Outage Time | 2 | TRIP | A/L/R | Temperature below P13.10 (P_OutsideAirMinTemp) for 60 sec, restart: Temperature above P13.10 (P_OutsideAirMinTemp) + 5°C
81 | Shaft bearing over temperature | AF Down Time | 2 | TRIP | A/L/R | Temperature above P13.12 (P_ShaftBearingTempMax) for 60 sec, restart: Temperature under P13.12 (P_ShaftBearingTempMax) – 15°C (only from GEWE1.5s)
82 | Yaw motor over temperature | AF Down Time | 2 | TRIP | A/L/R | One of the 4 PTC-temperature sensors on yaw motors report excessive temperature (> 155°C)
84 | Gearbox oil temperature too low | OK OK Time | 2 | OK | A/L/R | Min. temperature of gearbox oil sump and bearing A below P13.7 (P_GbxOilTempMin) for 10 minutes Restart: temperature equal to or above P13.7 (P_GbxOilTempMin) for 10 minutes
86 | Secondary brake pads worn | AF Down Time | 2 | TRIP | L/R | Brake lining worn for 20 sec
87 | Restart time delay | OK OK Time | 2 | OK | A | Set after grid loss, temperature errors, storm and calm, period P8.1 (P_StartupDelayTime)
88 | Multiple sensor over temperatures | OK OK Time | 0 | OK | L/R | Max number of temperature errors (P13.11 (P_RestartAfterFaultTemp)) exceeded. (Errors 75-77, 81, 98-100, 107, 115, 139)
89 | Dirty Gearbox oil filter (warning) | OK OK Time | 0 | OK | L/R | Filter soiled (fine) for period P10.6 (P_GbxFilterTime) and for gearbox oil temp, > 50°C or Filter soiled (combi filter) for period P10.6 (P_GbxFilterTime) for gearbox oiltemperature > P10.14 (P_GbxFiltrationOnTempMin)
91 | Gearbox warm up | OK OK Time | 0 | OK | L/R | Gearbox oil temperature < P10.7 (P_GbxFullLoadOpOilTempMin) (min. temperature gearbox nominal load
94 | Control call to SCADA | OK OK Time | 0 | OK |  | Scada support, updated requirement
97 | Generator cooling air over temperature | AF Down Time | 2 | TRIP | A/L/R | Temperature above P13.6 (P_GenInternalAirTempMax) for 60 sec, restart: temperature below P13.6 (P_GenInternalAirTempMax)- 15°C
98 | Gearbox bearing over temperature | AF Down Time | 2 | TRIP | A/L/R | Temperature above P13.9(P_GbxBearingATempMax) for 60 sec, restart: Temperature below P13.9(P_GbxBearingATempMax) – 15°C
99 | Generator stator over temperature winding 1 | AF Down Time | 2 | TRIP | A/L/R | Temperature above P13.1 (P_OutsideAirMinTemp) for 60 sec, restart: Temperature below P13.1 (P_OutsideAirMinTemp) – 15°C
100 | Generator stator over temperature winding 2 | AF Down Time | 2 | TRIP | A/L/R | Temperature above P13.1 (P_OutsideAirMinTemp) for 60 sec, restart: Temperature below P13.1 (P_OutsideAirMinTemp) – 15°C
101 | DTA/MCC Fuse or Motor protection alarm | AF Down Time | 2 | TRIP | L/R | SM_Envr_ControlBreakerDTA generated when 24V fuse protection in MCC control box tripped
102 | Top Box Fuse or Motor protection alarm | AF Down Time | 2 | TRIP | L/R | SM_Envr_ControlBreakerTB generated when motor protection in topbox cabinet tripped
105 | Converter rotor voltage fault | AF Down Time | 14 | TRIP | A/L/R | voltage error, CCU generator side
106 | Converter rotor current fault | AF Down Time | 14 | TRIP | A/L/R | Current error, CCU generator side
107 | Converter rotor temperature fault | AF Down Time | 14 | TRIP | A/L/R | Temperature error, CCU generator side
108 | Rotor lock engaged | AF Down Time | 6.3 | TRIP | L/R | One of the rotor locks is engaged
110 | Speed in the tower resonance range | OK OK Time | 14 | OK | A/L/R | 1. If generator speed from CCU > resonance low limit + 10 AND < upper limit - 10, a timer will be initiated and timer value will be outputed. 2. If timer value exceeds a threshold, set fault. 3. If generator speed from CCU < 300, reset fault. 4. If general reset command = TRUE AND it is not the first cycle of PLC AND it exceeds 5 sec delay from reboot, reset fault. 5. Reset condition has lower priority than set condition.
112 | Invalid converter respose | AF Down Time | 14 | TRIP | A/L/R | Control and (acknowledgement freq. Converter AND acknowledgement main switch) differ for 65 sec
113 | Line side CCU voltage fault | AF Down Time | 14 | TRIP | A/L/R | Voltage error CCU line side
114 | Line side CCU current fault | AF Down Time | 14 | TRIP | A/L/R | Current error CCU line side
115 | Line side CCU temperature fault | AF Down Time | 14 | TRIP | A/L/R | Temperature error CCU line side
116 | Grid voltage fault | NA Grid Outage Time | 14 | TRIP | A/L/R | Grid voltage error
117 | Grid frequency fault | NA Grid Outage Time | 14 | TRIP | A/L/R | Line frequency error and grid voltage > 15% of P20.14 (P_VoltageNominal rated grid voltage)
118 | Emergency stop nacelle / hub | AF Down Time | 6.3 | TRIP | L/R | Emergency off top-box/hub activated
120 | Pitch controller communications fault | AF Down Time | 14 | TRIP | L/R | Main controller does not receive heart beat signal from pitch axis 1 (WEPA board) and pitch axis 2 (WEPA board) and pitch axis 3 (WEPA board) in 1.25s
121 | Axis 1 pitch controller fault | AF Down Time | 14 | TRIP | A/L/R | Pitch controller reports axis disturbance for a period P12.12 (P_PitchTimeOfDisturbance)
122 | Collective fault pitch controller | AF Down Time | 14 | TRIP | A/L/R | Pitch controller reports unit disturbance for a period P12.12 (P_PitchTimeOfDisturbance)
124 | Pitch Overrun 0deg | AF Down Time | 14 | TRIP | L/R | At least. 1 rotor blade at limit switch (- 8°) delayed by 4 of 10 samples
125 | Pitch Overrun 90deg | AF Down Time | 14 | TRIP | L/R | At least. 1 rotor blade at limit switch (87°) delayed by 4 of 10 samples
127 | Synchronizing switch maintenance required | OK OK Time | 0 | OK | L/R | Number of cut-ins of synchronization switch exceeds max. Number P26.15 (P_CuCbSwitchCountMax) at which the switch contacts should be checked.
129 | Generator speed not plausible | AF Down Time | 14 | TRIP | A/L/R | Deviation P1.6 (P_SpdDevMax)between generator / gearbox speeds exceeded for period P1.7 (P_SpdDevPeriod).and (generator speed exceeds P1.11 (P_GenSpdMonMin)or rotor speed exceeds P1.11 (P_GenSpdMonMin) / P1.5 (P_GenRotSpdRatio)). Or if there is a downwind detected momentarily and to avoid the rotor from turning counter clockwise direction. During the later, the gen speed threshold for monitoring is not valid.
130 | Braking time rotor blade 1 too high | AF Down Time | 6.2 | TRIP | L/R | Drive time P8.5 exceeded during battery drive up to spinning position (P12.2 - P_PitchRateAfterCutIn) or angle difference between second 2 and 5 of battery drive less than P8.9 (P_Pitch3sAngDiffInBattDrv) for blade 1.
131 | Braking time rotor blade 2 too high | AF Down Time | 6.2 | TRIP | L/R | Drive time P8.5 exceeded during battery drive up to spinning position (P12.2 - P_PitchRateAfterCutIn) or angle
132 | Braking time rotor blade 3 too high | AF Down Time | 6.2 | TRIP | L/R | Drive time P8.5 exceeded during battery drive up to spinning position (P12.2 - P_PitchRateAfterCutIn) or angle difference between second 2 and 5 of battery drive less than P8.9 (P_Pitch3sAngDiffInBattDrv) for blade 3.
133 | Batteries Charging | AF Down Time | 2 | TRIP | A | Battery charging at standstill for period P8.8 (P_PitchBattChargingTime), After message ‘battery voltage too low’, ‘battery charging voltage not OK’ or ‘braking time blade 1, 2 or 3 too long’, delayed by 1sec
134 | Battery charging voltage not OK | AF Down Time | 2 | TRIP | L/R | Battery charging voltage not OK, delayed by 10 sec
135 | Emergency Brake System Test | OK OK Time | 2 | OK | A/L/R | Emergency braking system test is performed under certain conditions. See section 4.2.3
136 | 0 deg limit switch failure | AF Down Time | 14 | TRIP | L/R | One limit switch axis has tripped but current blade angle of tripped blade is > -8°, delayed by 8 of 24 samples
137 | 90deg limit switch failure | AF Down Time | 14 | TRIP | L/R | One limit switch axis has tripped but current blade angle of tripped blade is < P12.1 (P_PitchFeatherPos) (feathered position), delayed by 8 of 24 samples
138 | Pitch motor overtemperature warning | OK OK Time | 0 | OK | L/R | Warning temp exceeded for at least 1 pitch axis
139 | Pitch motor overtemperature alarm | AF Down Time | 2 | TRIP | A/L/R | Maximum temperature exceeded for at least 1 pitch axis
140 | Motor protection pitch motor | AF Down Time | 14 | TRIP | L/R | Motor protection activated from at least one pitch motor
141 | Rotor CCU collective faults | AF Down Time | 14 | TRIP | A/L/R | Other errors CCU - generator side
142 | Line CCU collective faults | AF Down Time | 14 | TRIP | A/L/R | Other errors CCU - line side
143 | Overspeed monitor failure | AF Down Time | 2 | TRIP | L/R | No pulses to overspeed monitor for 10 sec, if gen. Speed P1.11 (P_GenSpdMonMin) is exceeded
144 | Blade angle asymmetry | AF Down Time | 14 | TRIP | A/L/R | Deviation of 2 blade angles for a period or 4° for 200msexceeded in automatic pitch control mode.
145 | Pitch control deviation axis 1 | AF Down Time | 14 | TRIP | A/L/R | Deviation P12.7 (P_BladAngDeviationMax) of blade angle 1 current value and demand value for a period P12.8 (P_PitchCtlDeviationTimeMax) or in
146 | Low wind speed cut out | WE Weather Outage Time | 2 | TRIP | A/L/R | Below 15% of speed P2.1 (P_SpinningSpdStart) when spinning, 30 sec time delay, reset for exceeding wind 3.0 m/sec at standstill
147 | Load shutdown | OK OK Time | 2 | OK | A | Command load shutdown from turbine Web Page causes shutdown in feathered pitch position
148 | Generator fan service switch | WA Maintenance Time | 0 2 after 30 min | TRIP | L/R | Service switch gen. Fan activated on top-box
149 | Axis 2 pitch controller fault | AF Down Time | 14 | TRIP | A/L/R | Pitch controller reports axis disturbance 2 for period P12.12 (P_PitchTimeOfDisturbance)
150 | Axis 3 pitch controller fault | AF Down Time | 14 | TRIP | A/L/R | Pitch controller reports axis disturbance 3 for period P12.12 (P_PitchTimeOfDisturbance)
152 | Aviation light failure | OK OK Time | 0 | OK | L/R | If P26.3 Bit6 (P_TwilightDetectionActivate) = 1: in case of a failure of 24V-supply or fault/failure signal of device within 30 sec Monitoring twilight switch: If P26.3.6 (P_TwilightDetectionActivate) =1 and between 0 AM and 1AM for 30sec
153 | Generator brushes worn | OK OK Time | 0 2 n. Zt. P8.1 1 | OK | L/R | Brush limit switch reports excessive wear after a period P8.11 (P_GenBrushWearDelayTime) the turbine is braked
155 | Maintenance | WA Maintenance | 0 2 after 30 min | TRIP | A | Service rotary switch is set to the ‘maintenance’ position. No remote commands are carried out. With a start command the turbine will restart for 30 minutes.
156 | Repair | RE | 0 2 after 30 min | TRIP | A | Service rotary switch is set to ‘repair’ position. No remote commands are carried out. With a start command the turbine will restart in 30 minutes.
157 | Secondary rotor brake does not close | AF Down Time | 14 | TRIP | L/R | 3 sec after applying active brake, feedback indicates brake still released
161 | Overvoltage protection fuse | OK OK Time | 0 | OK | L/R | Faulty overvoltage protection device in main or top switch cabinet and cannot
163 | Torque deviation | AF Down Time | 2 | TRIP | A/L/R | Assigned torque demand and power are implausible. Deviation converted to kW: 200 delayed by 30 sec. It is not monitored if CCU signals a torque reduction (#287)
164 | Pitch maintenance switch | WA Maintenance Time | 2 | OK | A/L/R | Enabled maintenance switch which separates batteries from pitch motor on axis box, delayed by 500 msec
165 | Pitch service switch | WA Maintenance Time | 2 | OK | A | Switch setting at the control box Hub is in manual operation, blade adjustment is possible from the controller, without an error or assigned demand from turbine controller delayed by 500 msec (See also SM 365 “Service switch pitch implausible”)
166 | Normal operation | OK OK Time | 0 | OK | A | Signals end of: low noise operation, stop by an external device, ice alarm, direction-dependent shut-down
167 | Voltage limiting mode active | OK OK Time | 0 | OK | A/L/R | Voltage is limited by assignment of an inductive reactive power < 1, phi < 0° and /or power limitation
168 | Yaw emergency stop | OK OK Time | 0 | OK | L/R | SM 168 is always activated together with SM 28. The nacelle is driven 90° out of the wind. An attempt is made to move to the right. Unless cable unwinding would be activated in the right sector, the nacelle is driven to the left.
169 | Gearbox oil pressure startup delay | OK OK Time | 2 | OK | A/L/R | When oil pump on, P10.1 (P_GbxOilPressureLowTime) (delay time oil pressure gearbox) > 70 sec and curr. Delay time > 5 sec. Note reason turbine does not start after START button has been activated
170 | Increasing speed with falling blade angle | AF Down Time | 6.2 | TRIP | L/R | Monitoring pitch / generator speed gradient: 50 ms-averaged speed increases with falling blade angle -> delays for period P26.5 (P_DelayTimeSpdRiseBladFalling) in ms, or too high generator speed (>300rpm with pos. gradient, > 600Upm, resp.) blades in feathered position
171 | Service key brake release | OK OK Time | 2 | OK | A/L/R | When activating the button ‘release brake’ on the top-box in the feathered pitch position. Message remains 30 sec after releasing button
172 | Shut down for stall ice detection | WE Weather | 2 | TRIP | L | Ice sensor detects or indicates low temperature and high humidity (Outside temp. < 3°C). Possibility of icing at rotor blades. Shut down for Ice Detection with low power can be activated by P48.19, bit 3 and will monitor power reduction due to ice stall. Power reduction requires parameter setup P48.4 - P48.10
173 | Low-noise | OK OK Time | 0 | OK | A | Turbine runs with reduced rotor speed and power, limited by P27.1 (P_NroRotorSpdSetPoint) and P27.2 (P_NroPowerMax) or it runs with increasedtorque/speed characteristic in partial load, defined with factor P5.13 (P_FactorTorqCharNro) > 100%. Both features are activated by digital input (see section 4.3.1).
174 | Over | OK OK Time | 0 | OK | A/L/R | When transformer temperature monitoring device reports warning, its contact input to controller turns true, delay 200 ms.
175 | Over | AF Down | 2 | OK | A/L/R | When transformer temperature monitoring device reports error, its contact input to controller turns true, delay 200 ms. Restart condition: contact input turns false, delay 200 ms.
176 | Drive train | AF Down | 2 | TRIP | A/L/R | Drive train acceleration > wind speed dependent characteristic for period P7.10 (P_DrvTrOscAlmDelayTime) and P7.12 Bit 15 (P_DrvTrVibrationSpdCalcEnable) = 1
177 | Tower vibration | AF Down | 14 | TRIP | A/L/R | Accelerometer monitors the frequency range around the tower’s resonance frequency. Alarm if (P7.12 bit 1 (P_TowerVibrationDIEnable) =1) or tower acceleration > P7.7 (P_TwrVibrationAccelAlarmThrsh) for period P7.8 (P_TwrVibrationAlmDelayTime) and P7.12 bit 0 (P_TowerVibrationAIEnable) = 1
179 | Successful |  | 2 | TRIP | A | A disturbance of emergency pitch system was detected (SM130-132, 134, 212-214). A reset of this fault is not possible until a successful emergency braking system test (activated by setting P23.12 (P_TestTrigger) =1) is done.
180 | Nacelle wind direction tracking error | OK OK Time | 2 | OK | A/L/R | 1 sec-average wind direction deviation value > P7.5 (P_WindDeviation1SecMax) or 10sec average value > P7.6 (P_WindDeviation10SecMax) and 4min- average wind speed > 7 m/s and turbine online
181 | Spinning position | OK OK Time | 0 | OK | A | Turbine in spinning mode
182 | Start-up | OK OK Time | 0 | OK | A | Turbine starting up /noload mode
183 | Load operation | OK OK Time | 0 | OK | A | Turbine in load operation
184 | Shut down | OK OK Time | 2 | OK | A | Turbine shutdown (braking)
185 | Manual pitch operation | OK OK Time | 2 | OK | A | Manual blade adjustment with pitch rate P12.5 (P_PitchRateInManual) (control function –blade angle or operating function at the top-box operating device )
186 | Manual speed operation | OK OK Time | 0 | OK | A | Manually assigned generator speed in idling mode (control function –speed)
187 | Manual torque operation | WA Maintenance Time | 0 2 after 30 min | OK | A | Manually assigned torque in load operation (control function –freq. Converter), if 30min manual operation the turbine is braked
188 | Manual line disconnected operation | WA Maintenance Time | 0 2 after 30 min | OK | A | Manual grid separation (control function – frequency converter) Speed control to setpoint P3.4 (P_LoadGenSpdMin) in idling mode, if 30min manual operation the turbine is braked
189 | Manual yaw operation | WA Maintenance Time | 0 2 after 30 min | OK | A | Manual yaw adjustment or yaw blocking with service switch (control function – general)), if 30min manual operation the turbine is braked
191 | Manual generator fan operation | WA Maintenance Time | 0 2 after 30 min | OK | A/L/R | In manual operation from Web Pages, fan is then permanently on or off, if 30min manual operation the turbine is braked
193 | Aviation light alarm | OK OK Time | 0 | OK | A/L/R | SM 193: SM_Envr_ObstructionLightMalFun is triggered after PLC reboot in case of extern obstruction light signal malfunction for 5 sec OR judgment of twilight switch .It indicates the aviation light system is still in operation but needs service.
194 | Sump by-pass filter clogged | OK OK Time | 0 | OK | L/R | if oil sump temp. > (P14.13 (P_GbxOpByPassFilterTempMin)+ P14.14
195 | Gearbox by-pass filter low pressure warning | OK OK Time | 0 | OK | L/R | If by-pass filter pump is switched on and low pressure (pressure switch) longer than 10 sec -> switch off by- pass filter pump
201 | IO Card 28V power supply failed | AF Down Time | 14 | TRIP | L/R | External 24V-power supply to at least one module of the control unit has failed. Possible error also defect module on 24V-side.
203 | Temperature measurement system fault | AF Down Time | 2 | TRIP | L/R | All temperature measurement are constant for 10 minutes (resolution 0.1°).
205 | Cabinet over temperature | AF Down Time | 2 | TRIP | A/L/R | Main or top switch cabinet temperature above P34.13 (P_CabinetsTempMax ) or any hub switch cabinet temperature above P34.14 (P_HubCabinetsTempMax) (GE pitch) or one of these temperature above these threshold + 10K for 60 sec, restart: temperature below threshold value – 2K. (For GEWE1.X-100m CWE, also special CWE document SM313)
207 | Ground fault | AF Down Time | 2 | OK | L/R | EM207 delayed by P20.13 (GEWE1.5/70.5 (60Hz) only)
208 | Converter communication failure | AF Down Time | 14 | TRIP | L/R | Life sign stays constant for a period of 150ms -> IONET connection interrupted / disturbed or CCU switched off. No monitor in the first 20sec after rebooting turbine controller.
212 | Battery voltage not OK axis 1 | AF Down Time | 2 | TRIP | L/R | Battery voltage too low for axis 1
213 | Battery voltage not OK axis 2 | AF Down Time | 2 | TRIP | L/R | Battery voltage too low for axis 2,
214 | Battery voltage not OK axis 3 | AF Down Time | 2 | TRIP | L/R | Battery voltage too low for axis 3
215 | Wind direction dependent shut- down | WR Wind Direction Curt Time | 2 | TRIP | A/L/R | Nacelle position is inside direction range defined by P27.4-8 and P > P27.9 (P_WndCurtPowerMax) or v > P27.10 (P_WndCurtMaxAvgWndSpd4Min), restart if v < P27.11 (P_WndCurtResetAvgWndSpd4Min) or Nacelle position is outside the direction range.
218 | Frequent cut-ins observed | OK OK Time | 0 | OK | L/R | For a period of one hour and one day the number of cut-ins are counted. If these numbers are greater than P26.13 (P_CuCbSwitchPerHourMax) or P26.14 (P_CuCbSwitchPerDayMax), a warning
221 | External power limitation | OK OK Time | 0 | OK | L/R | External command from park-PC or park management controller with max. power demand
222 | Yaw runaway | AF Down Time | 2 | TRIP | L/R | Nacelle is turning without yaw motor activation by angle > P11.13 (P_YawRunawayMax).
223 | Blade angle not plausible axis 1 | AF Down Time | 14 | TRIP | L | Blade angle 1 out of allowed range - 8°..93° or jump of current value, for more than 1 sec.
224 | Circuit breaker feedback error | AF Down Time | 2 | TRIP | L/R | If CB1 separated from synchronization conductors, there are no correct feedback signals from CB1: 1. Ready signal, if safety chain closed, no CCU fault and CB1 open, delay 10 sec 2. ON signal, if CB1 should close at the transition to spinning mode, delay 1 sec,
235 | Main circuit breaker tripped | AF Down Time | 14 | TRIP | L/R | Error message is coming from Frequency converter.
237 | Generator over temperature winding 3 | AF Down Time | 2 | TRIP | L/R | If temperature rise >= “P_GenWindingTempMax” for a period of 60 seconds status message“SM 237” is triggered. If temperature falls below temperature hysteresis of “P_GenWindingTempMax” –15 degree status message should reset automatically.
238 | MVSG CB Open | OK OK Time | 14 | OK | A | MVSG CB is open, delay 200ms.
247 | Cable supervision pitch motor | AF Down Time | 14 | TRIP | L/R | DI_In_PitchMotor2CableSupervision signal triggered on WEPA
250 | Temperature sensor error (shut down) | AF Down Time | 2 | TRIP | L/R | Temperature sensor, which is important for turbine control, is defective (cable break or short circuit),
251 | Temperature sensor error (warning) | OK OK Time | 0 | OK | L/R | Temperature sensor, which is not important for turbine control, is defective (cable break or short circuit, resp.) or comparable temperatures have a excessive deviation (P13.20 (P_TempCompareMax)),
252 | Temperatures not plausible (shut down) | OK OK Time | 0 | OK | L/R | Comparable temperatures (such as winding 1 + 2 + 3,) deviate by more than P13.20 (P_TempCompareMax) (=20deg C) for one minute,
257 | Manual operation bearing lubrication | WA Maintenance Time | 2 | OK | L/R | Manual operation of main and yaw bearing lubrication.
258 | Gearbox manual operation | WA Maintenance Time | 2 | OK | L/R | If pitch set to feather position and gearbox mode is auto mode in last cycle and command gearbox manual operation, raise the SM258.
261 | Manual Hydraulic / Brake | WA Maintenance Time | 2 | OK | A | SM_DrvTr_BrakeHydManu is set to 0 in 1.X-100m wind turbine.
263 | Manual Gen. heating | WA Maintenance Time | 2 | OK | A | Stop turbine in case of manual heater operation. Manual operation allows service maintenance and test generator heater in a controlled and safe condition.
266 | Voltage asymmetry Alarm from CCU | Line Out Time | 14 | TRIP | A | Only for NGG: The Converter is reporting asymetric voltage Alarm (DI_In_CuGridVoltAsymFault)
267 | Generator Base Vibration | System Down Time | 2 | TRIP | L/R | Acceleration transducer (PCH) reports via Profibus Bus vibration alarm: Digital monitoring (P7.12.bit1 (P_TowerVibrationDIEnable) = 1) * digital generator base frame vibration lateral * digital generator base frame vibration vertical Analog monitoring (P7.12.bit0 (P_TowerVibrationAIEnable) = 1) * generator base frame acceleration (lateral) > P7.15 (P_OpCtlBFAlarmThresholdLateral) for period P7.08 (P_TwrVibrationAlmDelayTime) * generator base frame acceleration (vertical) > P7.18 (P_OpCtlBFAlarmThresholdVert) for period P7.08 (P_TwrVibrationAlmDelayTime)
269 | Reboot PLC | OK OK Time | 2 | OK | A/L/R | Turbine controller is rebooted, because of a user command. Before this turbine is stopped with BP 2.
270 | Fire alarm | AF Down Time | 14 | TRIP | L | SM_Envr_FireAlarm is generated when smoke and/or heat exceeding an alarm threshold has been detected by fire detection equipment
271 | Gearbox particle counter malfunction | OK OK Time | 0 | OK | L/R | Malfunction particle counter SM 271:"SM_Gbx_ParticleCounterMalFct" No digital ok signal "DI_In_TbGbxOilParticleCounterOk" = 0 and particle counter is enabled over parameter "P_GbxParticleCounterMonEn" for a period of 1sec.
272 | Shadow related shut down | EX External Stop Time | 2 | TRIP | A | WTG is stopped due to a signal of shadow module Only active when P26.3 Bit11 (P_ShadowModuleEnable) = TRUE
273 | Manual / service | RE Repair | 2 | OK | A | Message appears if WTG is switched off
274 | Pitch thyristor 1 fault | AF Down | 14 | TRIP | L/R | Pitch Thyristor 1 not ready, although grid contactor has been switched on for minimum 700 ms and grid voltage > P20.2 (P_LineVoltageMin). If this message appears, fuse 1F1 in axis cabinet may be defective
275 | Pitch thyristor 2 fault | AF Down | 14 | TRIP | L/R | Pitch Thyristor 2 not ready, although grid contactor has been switched on for minimum 700 ms and grid voltage > P20.2 (P_LineVoltageMin). If this message appears, fuse 1F1 in axis cabinet may be defective
276 | Pitch thyristor 3 fault | AF Down | 14 | TRIP | L/R | Pitch Thyristor 3 not ready, although grid contactor has been switched on for minimum 700 ms and grid voltage > P20.2 (P_LineVoltageMin). If this message appears, fuse 1F1 in axis cabinet may be defective
277 | Temperature | OK OK Time | - | OK | A/L/R | Message is set if there is an active power limitation because of a high temperature of one or more devices (see P37.3 – 6), or because of low ambient temperature
278 | Shut-down low | NA Grid | 14 | TRIP | A | If grid voltage (nominal value P20.14 - P_VoltageNominal) is between P20.16 (P_UnderVoltage1Min) (% of nominal voltage) and P20.15 (P_UnderVoltage1Max) (% of nominal voltage) for a period of P20.17 (P_LVRTComsumerOFFTime) or less than P20.16 (P_UnderVoltage1Min), auxiliary systems (yaw motors, fans, heaters, pumps, etc.) are shut off as part of LVRT mode, activated with P26.3 Bit 13=1). Auxiliary systems can only be shut off for a limited period of time P20.18 (P_LVRTShutDownTime). Once this time period has been exceeded, turbine shuts down with message 278. If grid voltage exceeds P20.15 (P_UnderVoltage1Max) auxiliary systems are switched on with a 2 sec time delay and WTG is restarted automatically.
279 | Low voltage ride through | OK OK Time | 0 | OK | A | Grid voltage (nominal value P20.14 - P_VoltageNominal) is between P20.16 (P_UnderVoltage1Min) (% of nominal voltage) and P20.19 (P_VoltageLVRTMin) (% of nominal voltage) for less than P20.20 (P_LVRTTimeMax) seconds and (only in LVRT mode, activated with P26.3 Bit 13=1 (P_LVRTmodeEnable)). This is an indication that LVRT grid conditions have been detected. Turbine will shut down if grid voltage falls below minimum grid voltage for ride through (P20.19 (P_VoltageLVRTMin)) or maximum time for ride through (P20.20 (P_LVRTTimeMax).) is exceeded.
280 | Hydraulic brake test accumulator pressure error | AF Down Time | 2 | TRIP | L/R | During test of hydraulic system for active brake accumulator is tested. Pressure exceeds P9.13 (P_BrakePrePressureMax) or drops below P9.15 (P_BrakePrePressureMinFault) after (1 min). This is caused by a defect of accumulator. After resetting and restart test is repeated.
281 | Hydraulic brake test accumulator pressure warning | OK OK Time | 0 | OK | L/R | During test of the hydraulic for active brake accumulator is tested. Pressure is between P9.14 (P_BrakePrePressureMinWarning) and P9.15 (P_BrakePrePressureMinFault) after (1 min). Accumulator should be checked.
282 | Hydraulic brake test | OK OK Time | 2 | OK | A/L/R | During monthly test of hydraulic for active brake bubble storage is tested for 1 minute without hydraulic pump, start condition depends on day of month: 1-15: start test only before starting WTG (before leaving blade feathered position) 16-27: start test at low wind speed (<3m/s) 28-31: start test at any wind speed. Test can be interrupted by manual or emergency stop.
286 | Converter crow bar triggered | OK OK Time | 0 | OK | A/L/R | CCU has triggered crowbar protection circuit.
287 | Converter power limitation | OK OK Time | 0 | OK | A/L/R | CCU cannot produce level of power (torque) requested by main controller. This will occur during certain grid conditions.
288 | Brake battery pitching contact incorrectly active | AF Down Time | 14 | TRIP | L/R | Feedback signal from “interrupt battery driven pitching” is not set for more than 1 sec during a period where interruption of battery pitch is not commanded. Feedback signal is normally high and can be read on “status pitch” parameter page. If this bit is low for more than 1 sec it indicates that battery pitch is being interrupted without an interrupt command. This is a safety concern since emergency pitch braking cannot function and turbine is shut down. Check the status of signal in Web page and if necessary check “signal break battery run disable” circuit starting in main pitch controller panel and running through each axis panel.
289 | Measurement system test | OK OK Time | 2 | OK | A | In case of connected measuring system tests for calibrating blade and tower sensors are executed in low wind situation. This test is configurable with P18.13-19.
290 | Idling in speed control | OK OK Time | 0 | OK | A | Turbine is in idling mode with 300 rpm generator speed if min. temperature of gearbox oil sump and bearing A lower than P13.7 (P_GbxOilTempMin) (message 84 active). This idle mode is used to warm up gearbox. Status message 290 is shown. Following conditions must also be fulfilled: Failure-free automatic mode, blade angle in feathered position, outside temperature must allow start and the wind speed must be greater than 3,5 m/s. This idling mode is only activated, if the status messages 290 and 84 are both activated.
291 | Cabinet undertemperatur e | AF Down Time | 2 | TRIP | L/R | One of the cabinet temperatures (main, top, control, axis, battery cabinets) is below the value specified in P35.12 (P_ControlCabTempMin) ‘Min. temp control cabinet’ for a time longer than 60s. Restart if temperatures > P35.12 (P_ControlCabTempMin) + 5K.
294 | Warning adv. controls sensor | OK OK Time | 0 | OK | A/ALC | One and only one of the MSF proximity sensors used for ALC has given a fault signature; this can be any of multiple low level characteristics - wire break, out of range high or low, large step, no
295 | Warm up state | WE Weather | 2 | OK | L/R | For CWE turbines: Coming from temperatures below, turbine will not start up until all substations of controller are started and all-important temperatures (cabinets, slipring and gearbox) are Ok. While turbine is stopped due to a temperature that is too low, error message 295: ’Heat up state’ is displayed. Availability counter ‘weather out time’ is increased.
297 | Turbine warm up error | AF Down | 2 | TRIP | L/R | For CWE turbines: If turbine is not heated up for operation after 8h of heat-up time (e.g. after a grid loss) error message 297 ‘Turbine heat up error’ is displayed and down-time counter is increased until turbine is ready to operate. Also this message is generated if turbine was heated up and a temperature falls below the allowed range.
299 | Loss of time | OK OK Time | 0 | OK | A/L/R | If the update period of timestamp is longer than P23.13 seconds, set the SM299. If the general reset command is issued AND it is not the first cycle of PLC AND it exceeds 5s delay from reboot, reset the fault.
301 | Malfunction | OK OK Time | 0 | OK | L/R | This is a warning about the generator lubrication has a malfunction. This is indicated by DI_In_TbGenLubricationOk staying TRUE for longer than 60sec while the lubrication is released with DO_Gen_TbLubricationOn set to TRUE. This monitoring is active if generator lubrication is enabled by P1003 (P_GenBearingLubEnable) = TRUE
302 | Brake pads worn (warning) | OK OK Time | 0 | OK | L/R | Brake pad wear sensor of rotor brake detects a warning.
304 | Combined | OK OK Time | 0 | OK | L/R | The main bearing lubrication grease tank is empty. This is indicated by the input (DI_In_TbCombLubrTankLevelOk) staying low for longer than 60sec. For combined lubrication system (main and yaw bearing P32.10.0 (P_DrvTr_EnableMainBearLub)=1.)
306 | Manual operation | WA | 2 | OK | A | SM_In_ManualHydraulik is not used in 1.6-100m wind turbine.
308 | Idling command | OK OK Time | 2 | OK | A | Pushbutton ’Idle’ at main switch cabinet is pressed or key ‘Idle’ on general control function of web page. The WTG is shut down without
310 | Fault reset | OK OK Time | 0 | OK | A | If fault(s) are active and a manual reset is given this message is active for 500ms.
311 |  | OK OK Time | 0 | OK | L/R | SM_Envr_FireAlarmWarning is
312 | Fire alarm sensor error | OK OK Time | 0 | OK | L/R | SM_Envr_FireAlarmSensorError is generated when fire detection system has detected a problem with the sensor(s).
313 | Cabinet over | OK OK Time | 0 | OK | L/R | For CWE turbines: main or top switch cabinet temperature above P34.13 (P_CabinetsTempMax ) or any hub switch cabinet temperature above P34.14 (P_HubCabinetsTempMax) (GE pitch) or above P34.13 (P_CabinetsTempMax ) (SSB pitch) for 60 sec, restart: temperature below threshold value – 2K. (for GEWE1.X- 100m CWE, s. also special CWE document a. SM205)
314 | Power limitation | OK OK Time | 0 | OK | A/L/R | At high grid frequency there could be a power limitation. For more information see the parameter description documentP18.2 (P_FrequencyPowerLimitationMax), P18.3 (P_FrequencyPowerLimitationMin) and P18.5 (P_SlopePowerLimitOverFreq).
315 | Intrusion alarm | OK OK Time | 0 | OK | A | Door of plant is open and light in tower is off. Only active when P26.16, Bit 8 (P_Custom_IntrusionDectEnable) =1. Detailed description in a separate document: DECIO_Description_GEWE1.5.doc
316 | Intrusion | OK OK Time | 0 | OK | A | Intrusion detection is active (P26.16 Bit8 (P_Custom_IntrusionDectEnable) = 1) and it was disabled for more than 1h by switch-on of tower light. Detailed description in a separate document: DECIO_Description_GEWE1.5.doc
317 | Slip ring under temperature | WE Weather | 2 | TRIP | A/L/R | For CWE turbines: Temperature of slip ring (measured on PTAI12.5) is below P34.4 (P_SlipRingTempMin). Restart at temperature > P34.4 (P_SlipRingTempMin) + 5K. Setting P35.1
319 | Rotor lock active | OK OK Time | 2 | OK | A | SM_In_RotorLock is not used in 1.X- 100m wind turbine.
321 |  | OK OK Time | 0 | OK | A | SM_Yaw_YawBearLubFault generated
322 | Blade bearing | OK OK Time | 0 | OK | A | During activation of blade bearing lubrication pump the pressure has not built up (WEPA-H1-LubePress2PLC "DI_In_Blade1LubePressureSwitchOn") within max. pump time P32.19 (P_PitchBearingLubrMaxTime)
326 | limit switch | AF Down | 14 | TRIP | L/R | Current blade angle position indicates triggering of 93° limit switch not plausible, setting SM_Pitch_ExtFeathPosLmtSwitchDefec t = TRUE
327 | limit switch | AF Down | 14 | TRIP | L/R | Blade has moved past 87° limit switch and has triggered the 93° limit switch, setting SM_Pitch_ExtFeathPosOverRun = TRUE
328 | UPS fault | OK OK Time | 0 | OK | L/R | UPS Fault triggers if UPS feedback becomes FALSE for more than 240ms(the UPS feedback signal is lost more than 240ms, consider UPS has problem now)
329 | UPS deep battery discharge | OK OK Time | 0 | OK | L/R | UPS deep battery discharge triggers if low UPS battery becomes FALSE for more than 240ms(the low UPS battery signal is lost more than 240ms, consider UPS Battery discharged)
330 |  | OK OK Time | 0 | OK | L/R | SM_DrvTr_MainBearLubFault
332 | Vibration sensor |  | 0, 2 |  | A | Manual operation of vibration sensors (PCH) is selected by a control command in visualization program or operating panel. Test signals can be set with separate commands, test is performed to the same time for tower / base frame due to combined vibration monitor box
333 | Block restart due to grid condition | NA Grid | 2 | TRIP | A | Start is blocked with this message, if grid frequency > P38.15 or < P38.16 or grid voltage related to P20.14 > P38.17 or < P38.18 and WTG not online, Start is released again, if grid frequency and voltage is in normal range again for 30
334 | Circuit breaker maintenance necessary | AF Down Time | 2 | TRIP | L | Number of cut-ins of circuit breaker exceeds max. number P26.15 (P_CuCbSwitchCountMax) + 1000 at which switch must be maintained.
335 | Generator overspeed 2 | AF Down Time | 6.3 | TRIP | L | If generator speed exceeds level of P1.15 (P_GenSpdMaxHi), controller opens safety chain. This is redundant monitor for overspeed relay.
336 | Rotor overspeed 2 | AF Down Time | 6.3 | TRIP | L | If rotor speed exceeds level of P1.16 (P_RotSpdMaxHi), controller opens safety chain. This is redundant monitor for overspeed relay.
337 | Line CCU temperature warning | OK OK Time | 0 | OK | - | Message indicates IONet interface to CCU. Warning shows temperature warning of grid side CCU.
338 | Rotor CCU temperature warning | OK OK Time | 0 | OK | - | Message indicates IONet interface to CCU. Warning shows temperature warning of generator side CCU.
340 | Pitch control deviation Axis 2 | AF Down Time | 14 | TRIP | L/R | Deviation P12.7 (P_BladAngDeviationMax) of blade angle 2 current value and demand value for a period P12.8 (P_PitchCtlDeviationTimeMax) or in excess of 10° for 200ms in automatic pitch control mode. When braking 6 times the deviation from P12.7 (P_BladAngDeviationMax) is accepted.
341 | Pitch control deviation Axis 3 | AF Down Time | 14 | TRIP | L/R | Deviation P12.7 (P_BladAngDeviationMax ) of blade angle 3 current value and demand value for a period P12.8 (P_PitchCtlDeviationTimeMax) or in excess of 10° for 200ms in automatic pitch control mode. When braking 6 times the deviation from P12.7 (P_BladAngDeviationMax) is accepted.
342 | Blade Angle not plausible Axis 2 | AF Down Time | 14 | TRIP | L | Blade angle 2 outside permissible range -8°..93° or jump of current value, for more than 1 sec.
343 | Blade Angle not plausible Axis 3 | AF Down Time | 14 | TRIP | L | Blade angle 3 outside permissible range -8°..93° or jump of current value, for more than 1 sec.
344 | Pitch malfunction 2 or 3 blades | AF Down Time | 14 | TRIP | L/R | Malfunction of pitch system has been detected on more than one blade. Immediate switchover to battery drive. Error messages taken into account are: 121,149,150,145,340,341,223,342,343,3
345 | Battery drive after grid fault | AF Down Time | 14 | TRIP | L/R | Malfunction of pitch system is detected on at least one blade after a grid fault. Turbine is shut down with battery system.
346 | Rotor speeds not plausible | AF Down Time | 2 | TRIP | L/R | Deviation between both calculated rotor speeds is above P1.6 (P_SpdDevMax)% for time P1.7 (P_SpdDevPeriod).
347 | Base frame vibration power limiter active | OK OK Time | 0 | OK | A | The power and the speed of the turbine are reduced due to base frame vibrations, if this function is not disabled by P955 = 1 (P_TbBFVibPwrReductionDisabled). The reduction controlled in multiple steps: STEP1 The controller allows 5 BFV events in one hour. The 6th event in a hour will reduce the power by 29% of the nominal power. If no BFV occur in one hour in STEP1, control release STEP1 and teh limitation. STEP2 In this first limitation step, the controller allows 5 BFV events per hour again. The 6th event in a hour will reduce the power by 45% .If no BFV occur in one hour in STEP2, control switch to STEP1. STEP3 In the second limitation step, the controller shuts down the turbine after 6 more event occur in one hour.
348 | Service stop | OK OK Time | 2 | TRIP | A | P23.15 bit 0 (P_ServiceStopEnable) = 1 leads to SM348 with BP. 2 and rotor brake closed, WTG status OK.
349 | Service stop with fault | AF Down Time | 2 | TRIP | A | P23.15 bit 1 (P_ServiceStopFaultEnable) = 1 leads to SM349 with BP. 2 and rotor brake closed, WTG status is faulty.
350 | Service idle command | OK OK Time | 2 | TRIP | A | P23.15 bit 2 (P_ServiceIdle) = 1 leads to SM 350 with BP 2 and rotor brake open, WTG status OK,
351 | Service idle command with fault | AF Down Time | 2 | TRIP | A | P23.15 bit 3 (P_ServiceIdleFault) = 1 leads to SM 351 with BP 2 and rotor brake open, WTG status is faulty,
352 | Wind measurement serial communication fault | AF Down Time | 2 | TRIP | L/R | Serial communication with ultrasonic wind measurement device is disturbed
353 | Wind measurement device fault | AF Down Time | 2 | TRIP | L/R | Ultrasonic wind measurement device indicates unreliable values
355 | Power limitation fault adv.controls sensor | OK OK Time | 0 | LIMIT | A/ALC | If more than 1 MSF proximity sensor’s value shows an error signature, or ALC outputs from the rotor reset proximity sensor or PCH accelerometer show error signatures, this leads to collective ALC fault message SM 355 and turbine is in ALC protected mode.
357 | Grid voltage drop detected by converter | OK OK Time | 0 | OK | A/L/R | Transient voltage drop in grid was detected by the CCU
358 | Malfunction Triplepitch System | AF Down Time | 2 | TRIP | A | Minimum pitch rates (degrees/sec) not attained
359 | Pitch system in local operating mode | OK OK Time | 2 | OK | A | SM reflects internal special features of pitch control for GE Pitch System, e.g. initialization, search for reference, charging DC link. Pitch system is not ready for operation during this period.
360 | Incorrect conditions for pitch system local operating mode | AF Down Time | 14 | TRIP | L/R | If status message 359 appears in high- speed conditions (>500rpm) or if set longer than 120s this is deemed to be implausible and is indicated by status message 360.
361 | Power limitation adv.controls offsets | OK OK Time | 0 | LIMIT | A/ALC | If the system lacks a valid hub map (calibration), SM361 is set and turbine is in ALC protected mode.
362 | Calibrating ALC gains | OK OK Time | 0 | OK | A | ALCScales is active. During Scales procedure, message” SM362” is true. After procedure exit successfully or unsuccessfully, ” SM362” is false
363 | Mapping ALC offsets | OK OK Time | 0/1 | PAUSE | A | Hub mapping is active. During auto- stop to spinning state, SM363 is set. This message is automatically reset if turbine leaves for load state or faults occur during auto-stop
364 | Default MSF Sensor (none) based on parameter P_MSFProxSenso rType | OK OK Time | 0 | OK | A | SM364 is set after 1 sec of P_MSFProxSensorType = 0, SM364 will be false after 1 sec of P_MSFProxSensorType = 1/2/3 P_MSFProxSensorType = 0 for no sensor selected, 1 for 18mm sensors XS1M18AB120, Telemecanique; 2 for 30mm sensors, XS1M30AB120 Telemecanique; 3 for 12mm sensors range, Baumer sensors
365 | Service switch | AF Down | 2 | TRIP | L/R | Service switch pitch is switched on with
367 | CCU fault at abnormal grid condition | NA Grid Outage Time | 14 | TRIP | A/L/R | CCU fault is detected during abnormal grid condition (voltage and/or frequency out of normal range). This specific CCU fault is delayed by 200 msec and does not increase downtime then. SM367 counts to grid downtime.
368 | MSF bending out of threshold | AF Down Time | 2 | TRIP | L/R | Main shaft bending moment exceeds limitation. If hub mapping is completed and no ALC related errors, then check main shaft bending: if the DispD or DispQ is greater than P_DynCtl_ADVMSFBendingMax, then error message “SM368” occurs and turbine shut down with BP 2. This error message can only be reset manually or remotely
370 | Data trigger (stall) | OK OK Time | 0 | OK | A | Message 370 indicates that low power has been detected over the last P48.10 seconds. Averaged power is thereby compared with a reference characteristic defined by P48.4-9.
371 | Pitch limitation stall avoidance | OK OK Time | 0 | OK | A | TSR low power prevention adds an offset to minimum pitch limit that is determined from the ratio of measured TSR to known optimal TSR (P48.3 - P_TipSpeedRatioOptimal). Message 371 indicates that TSR algorithm has limited blade pitch for past 20 sec. This feature can be activated with P48.1 bit 0 (P_OpCtlTSRStallPreventEn) = 1
372 | Peak Shaver 2 active | OK OK Time | 0 | OK | A | Temperature and pressure conditions indicate usage of peak shaver 2 as configured, P48.13 (P_OpCtlPeakSh2StartTemp) –17 as opposed to original peak shaver defined with P17.4 and P17.10 (P_PitchMinPeakShaver). This feature can avoid low power due to air density dependent effects on rotor blade.
373 | Ice detected via stall | OK OK Time | 0 | OK | A | Low power is detected (see message 370) and ambient air temperature < P48.18 (P_OpCtlTempIceDetection). Low power may be caused by ice- foundation on the blades. If P48.19 bit 3 (P_OpCtlIceDetectionStop) = 1 then additionally ice alarm 172 is set and WTG is shut down.
376 | Short term error wind measurement device | OK OK Time | 0 | OK | A | SM_In_WarningUltrasonic - ultrasonic wind measurement device seems to have a sensor fault. Wind speed is set to the value 5sec prior to fault. Message dependent on P06.13.15 (P_DisableFaultHandlingUS) settings.
383 | Uncontrol battery test active | OK OK Time | 2 | TRIP | A/L/R | Uncontrolled battery test is currently active
384 | Long term error wind measurement device | OK OK Time | 0 | OK | A | SM_In_DisturbanceUltrasonic - ultrasonic wind measurement device has a sensor fault for more than 60sec with low wind or for a shorter time with high wind. Wind speed is set to the value 5sec before. *Speed is decreased to cut-in speed and power to 0kW. Message dependent on P06.13.15 (P_DisableFaultHandlingUS) settings.
386 | Communication fault pitch controller Axis 1 | AF Down Time | 14 | TRIP | A | Main controller not received heart beat signal from pitch axis 1 WEPA board in 250 ms
387 | Communication fault pitch controller Axis 2 | AF Down Time | 14 | TRIP | A | Main controller not received heart beat signal from pitch axis 2 WEPA board in 250 ms
388 | Communication fault pitch controller Axis 3 | AF Down Time | 14 | TRIP | A | Main controller not received heart beat signal from pitch axis 3 WEPA board in 250 ms
390 | Ice Sector based reduced speed/power operation | OK OK Time | 0 | OK |  | Is set, if turbine is in reduced operation due "Ice sector based reduced speed/power operation"
391 | AAB saturation | OK OK Time | 0 | OK | A | SM391 (SM_DynCtl_ABSaturation) aero balance saturation is set when RIC 0P actuation is at maximum value continuously for 10 min. Reset occurs after 1 min in non-saturated operation.
394 | YawMapPending | OK OK Time | 0 | LIMIT | A | If the system lacks a valid yaw map (calibration), SM394 is set and turbine is in ALC protected mode.
395 | YawMapping | OK OK Time | 2 | PAUSE | A | Indicate that yaw mapping is active
396 | YawMappingErro r | OK OK Time | 0 | LIMIT | ALC | During a yaw map calibration procedure an inconsistency in MSF proximity sensor readings greater than P_DynCtl_YawMap_Tolerance has occurred.
400 | Check Safety Chain | OK OK Time | 2 | OK | A | This message indicate, that a automatic safety chain check is in progress. The safety chain check is triggered after each hydraulic pre-pressure test (SM282). This Check can also be triggered manually by P23.12 (P_TestTrigger) = 22, when all blades are in feathered position and the safety chain is closed.
401 | Check Safety Chain Failed | AF Down Time | 2 | TRIP | L/R | The check of safety chain (SC) failed for one these reasons: - Safety chain does not open - Safety chain closes without time relay - Safety chain does not close again by resetting time relay
403 | Condition Monitoring System detected turbine problem warning | OK OK Time | 0 | OK | A | CMS Alarm (triggered when sensor acceleration value exceeds ADAPT.wind Farm Client Software Alarm threshold)
404 | Condition Monitoring System detected turbine problem fault | OK OK Time | 0 | OK | A | CMS Warning (triggered when sensor acceleration value exceeds ADAPT.wind Farm Client Software Warning threshold)
405 | Condition Monitoring System Malfunction | OK OK Time | 0 | OK | A | CMS Instrumentation Fault triggered when sensor fault occurs
411 | Avoid auto restart after grid error | NA Grid Outage Time | 2 | TRIP | L/R | If P38.20.14 is set and the controller restarts after a grid outage status is set. It can be reset by local or remote reset
412 | Power curve initialization missing | OK OK Time | 0 | OK | A | Settings for turbine type specific power curve are missing on parameter pages 63 and 64 and needs to be set. Available hard coded default settings are loaded on first PLC start or P19.20.02 (P_PwrCurvLoadDefault) = 1. In all other cases status message 412 is indicated.
413 | Yaw reference error | OK OK Time | 0 | LIMIT | ALC | If teeth counted yaw position deviates from yaw reference angle more than 9 degrees, reference angle is passed with no pulse, or during yaw mapping number of passing reference sensor < 2, set SM413.
414 | Power reduced operation | OK OK Time | 0 | OK | A | If power reduced while P4.4 < P4.1 (P_GenPowerDemandMax< P_RatedPower), set SM414, else if P4.4 > P4.1 (P_GenPowerDemandMax> P_RatedPower), reset fault.
416 | Max power reduced due to high air density | OK OK Time | 0 | OK | A | The max power is reduced dependent on high air density. This message is only shown if the reduced power is less then P4.4 (P_GenPowerDemandMax)
417 | WFMSCommunic ation when error and WT stop | OK OK Time | 0 | OK | A | WFMS communication is not OK and P_WFMScmdHoldEn=1, delay P_WFMSComTimeOut (5 sec), set SM417:SM_Curt_WFMScmdHold.
418 | CCU reports Safety chain open | AF Down Time | 14 | TRIP | A/L/R | DI_In_CuSafetyChainStop = TRUE and SM_In_SafetyChainOpen (SM63) = False, set SM418. For CCU faults (SM418~SM420), initiate BP 4 and increment turbine downtime. Auto reset strategy same as CCU collective faults (SM141, SM142).
419 | CCU reports Generator over speed | AF Down Time | 14 | TRIP | A/L/R | DI_In_CuGenOverSpeedTrip=TRUEand SM_DrvTr_GenOverSpeed (SM14) = False, set SM419. For CCU faults (SM418~SM420), initiate BP 4 and increment turbine downtime. Auto reset strategy same as CCU collective faults (SM141, SM142).
420 | CCU reports Generator under speed | AF Down Time | 14 | TRIP | A/L/R | DI_In_CuGenUnderSpeedTrip=TRUE, set SM420. For CCU faults (SM418~SM420), initiate BP 4 and increment turbine downtime. Auto reset strategy is same as CCU collective faults (SM141, SM142).
423 | At least one variable is forced in the system | OK OK Time | 0 | OK | A | If at least one digital IO is inverted through SCADA, SM423 is displayed
424 | System re- initialization after grid outage | OK OK Time | 0 | OK | A | Active after a grid outage event and clear after pre-defined time OR system status OK
425 | Low gearbox oil level detected | OK OK Time | 0 | OK | A | Oil low event detected by: 1, oil level of gearbox is too low for time P10.2 (P_GbxOilLevelLowTime). Monitoring begins if oil temperature is above P10.13 (P_GbxMonOilLevelOilTempMin), but not below 5°. 2, P_GbxExtendOPtime not passed since event occurred.
426 | Generator Lubrication – Long Term Fault | AF Down Time | 2 | TRIP | L/R | Generator lubrication long term fault generated after 2 weeks with warning SM301
427 | Hydraulic pump enable time too long warning | OK OK Time | 0 | OK | L/R | Hydraulic pump period above P9.5 (P_PumpOnTimeMax) (no pressure built up in the period) AND brake fault de- rating function enabled by command
428 | Hydraulic pump interval too short warning | OK OK Time | 0 | OK | A/L/R | Hydraulic pump interval period below P9.4 (P_PumpIntervalTimeMin) 6 times in a row AND brake fault de-rating function enabled by command
429 | Power derating due to mech. brake test pending | OK OK Time | 0 | OK | A | 1400 hours passed since last brake test, and turbine is running in de-rated condition
430 | Yaw tooth sensor | OK OK Time | 0 | OK | A | Yaw tooth sensor 1 fault
431 | Yaw tooth sensor 2 timeout | OK OK Time | 0 | OK | A | Yaw tooth sensor 2 fault
432 | Pitch system setup test required | OK OK Time | 2 | OK |  | 1. Message is set when any of below condition is met: AI_In_PitchCalibrationIDX = Pitchcal_TrackID_AxisX =0 Calibration ID Tracking for any Axis has changed A manual request for an emergency brake system test is initiated (C_In_PitchBatteryTest)
433 | Pitch system setup test active | OK OK Time | 2 | OK |  | Message is set when PSST test required is TRUE (432_SM_Pitch_PSSTRequired=1) AND all below conditions are FALSE 3_SM_OpCtl_ManualStop, 348_SM_In_ServiceStop, 349_SM_In_ServiceFaultStop, 47_SM_DrvTr_HydrTbServiceSwitchOn, 164_SM_Pitch_PitchMaitenance, 165_SM_Pitch_ServiceSwitchHub, 185_SM_OPCtl_HandPitch, 261_SM_DrvTr_BrakeHydManu, 7_SM_Envr_WindStormShutdown, 319_SM_In_RotorLock, 20_SM_Yaw_CableTwistingCw, OpCtl_BrakeProc5_or_6x_LL, 21_SM_Yaw_CableTwistingCcw, 434_SM_Pitch_PSSTFailAxisX=0
434 | Pitch system setup test failed for axis 1 | AF Down Time | 2 | TRIP | L/R | Message is set during SM433 (SM_Pitch_PSSTActive) or EBST test, if any below condition is met 1. 87° Limit switch not reached (DI_In_90DegLSAxis1) 2. -8° Limit switch not reached ( DI_In_0DegLSAxis1) 3. Pitch traverse range not between 99° and 107°.
435 | Pitch system setup test failed for axis 2 | AF Down Time | 2 | TRIP | L/R | Message is set during SM433 (SM_Pitch_PSSTActive) or EBST test, if any below condition is met 1. 87° Limit switch not reached (DI_In_90DegLSAxis2) 2. -8° degree Limit switch not reached ( (DI_In_0DegLSAxis2) 3. Pitch traverse range not between 99° and 107°.
436 | Pitch system setup test failed for axis 3 | AF Down Time | 2 | TRIP | L/R | Message is set during SM433 (SM_Pitch_PSSTActive) or EBST test, if any below condition is met 1. 87° Limit switch not reached (DI_In_90DegLSAxis3) 2. -8° Limit switch
437 | Pitch system setup test abort for axis 1 | AF Down Time | 2 | TRIP | L/R | Message is set during OpCtl_TurbineFullState_BT_L = 401, if blade angle1 (AI_In_PitchAngleCurrent1) not reached -2° in 40 Seconds
438 | Pitch system setup test abort for axis 2 | AF Down Time | 2 | TRIP | L/R | Message is set during OpCtl_TurbineFullState_BT_L = 403, if blade angle2 (AI_In_PitchAngleCurrent2) not reached -2° in 40 Seconds
439 | Pitch system setup test abort for axis 3 | AF Down Time | 2 | TRIP | L/R | Message is set during OpCtl_TurbineFullState_BT_L = 405, if blade angle2 (AI_In_PitchAngleCurrent3) not reached -2° in 40 Seconds
440 | Pitch Calibration Tracking ID changed for Axis1 | OK OK Time | 0 | OK | A | Message is set when Pitch Calibration Tracking ID changed for Axis1 (AI_In_PitchCalibrationID1)
441 | Pitch Calibration Tracking ID changed for Axis2 | OK OK Time | 0 | OK | A | Message is set when Pitch Calibration Tracking ID changed for Axis2 (AI_In_PitchCalibrationID2)
442 | Pitch Calibration Tracking ID changed for Axis3 | OK OK Time | 0 | OK | A | Message is set when Pitch Calibration Tracking ID changed for Axis3 (AI_In_PitchCalibrationID3)
443 | Blade Clearance Operating Mode | OK OK Time | 0 | OK | A | SM443 is enabled when tower acceleration is detected > threshold, SM180 occurred and degree-specified logic conditions are trigged. SM443 is disabled when wind speed is low in a specified time slot or a certain logic condition of SM180, SM177 and tower acceleration is trigged.
445 | Directional sector ice dependent shutdown | WE Weather Outage Time | 2 | TRIP | A | Message with BP 2 displayed when directional sector has been violated. During shutdown weather outage time should be incremented and turbine state set to bad weather condition. Message shall be reset if function is disabled, calendar control is not met or nacelle position is outside sector range. A manual override has been activated.
446 | Directional sector mode not safe | AF Down Time | 2 | TRIP |  | Set SM446 if status message SM31, SM60, SM222, SM415, SM430 or SM431 is active.
450 | Min. pitch angle exceeded |  | 6.3 | TRIP | Local | The 3 blades average pitch angle has been lower than the minimum pitch plus P41.10 (P_PitchMinOffsetMonitor) degrees and the 2 blades average pitch rate is less then -0.1 for longer then P41.11 (P_PitchMinExceededDelay).
451 | Manual brake | OK OK Time | 0 | OK |  | Manual brake test activated
452 | Manual brake | OK OK Time | 0 | OK |  | Manual brake test not executed due to wind turbulence
461 | Main bearing |  | 2 | TRIP | Local | SM_DrvTr_MainBearClogLong set when time passed since last successful injection (P32.13 + 4 months), trip turbine, disable pump and wait for service response
462 | Yaw bearing |  | 2 | TRIP | Local | SM_Yaw_YBLSysClogged set if 3 months pass since last successful yaw lubrication cycle.
466 | Initiate restart for pitch gear greasing | OK OK Time | 2 | OK | A | WTG is stopped for a short time and restarted for a pitch gear greasing procedure during run-up.
470 | Forced yawing | OK OK Time | 2 | OK | A | For combined lubrication system (main and yaw bearing): Automatic greasing for yaw bearing is only done when WTG is shut down and nacelle is turned one revolution. This message indicates when this procedure is active.
471 | Too long no | OK OK Time | 0 | OK | A | For combined lubrication system (main and yaw bearing): there was no greasing for 2 normal greasing periods in a row. Warning only is if there is a successful greasing cycle, no local/remote reset possible.
472 | Too long no | OK OK Time | 0 | OK |  | For combined lubrication system (main and yaw bearing): there was no greasing normal greasing period. Warning only is if there is a successful greasing cycle, no local/remote reset possible
478 | CCU not ready for operation | AF Down | 2 | TRIP | 3 | The signal ‘Ready for operation’ (DI_In_CuReady) from CCU is not set within 15s even Generator speed is above P03.08 (P_CutInGenSpeed) and then not falling below P01.12 (P_CutOutSpdDuringCutIn). This Monitoring becomes deactivated for 60s, after the main switch appies (DI_In_CuK1BrakeOn).
483 | Pitch gear | OK OK Time | 0 | OK | L/R | Pitch gear greasing is enabled via P12.14.11=1 or P12.14.12=1. Active pressure feedback signal is checked
487 | Fire Detection Pre alarm | AF Down | 2 | TRIP | Local | A fire detection system signals a warning and the turbine is configured to shut down in case of a fire warning (P26.16.03 P_FireWarningDeactivate =0).
489 | Bosch | OK OK Time | 2 | OK | A | The Bosch BLADEcontrol device has no valid reference date (B_Envr_BBCtrlAnaIceRes = FALSE) and ICE-Alarm is Monitoring enabled P48.19.10 (P_BBCtrlIceAlarmEn) = 1
490 | Bosch | OK OK Time | 0 | OK | A/L/R | The Bosch BLADEcontrol device set ICE- Alarm signal (B_Envr_BBCtrlIcingAlarm) to TRUE and ICE-Alarm is configured as warning P48.19.9 (P_BBCtrlIceWarningEn) = 1
491 | Bosch | WE Weather | 2 | OK | A/L/R | The Bosch BLADEcontrol device set ICE- Alarm signal (B_Envr_BBCtrlIcingAlarm) to TRUE and ICE-Alarm is configured as alarm P48.19.10 (P_BBCtrlIceAlarmEn) = 1
492 | Bosch | OK OK Time | 0 | OK | A/L/R | The ModBus communication to Bosch BLADEcontrol is failted (B_Envr_BBCtrlComOK = 0) or timed out (B_Envr_BBCtrlLifeSign = 0) and is configured as warning P26.20.8 (P_BBCtrlComAlarmEn) = 0
493 | Bosch |  | 2 | TRIP | A/L/R | The ModBus communication to Bosch BLADEcontrol is failted (B_Envr_BBCtrlComOK = 0) or timed out (B_Envr_BBCtrlLifeSign = 0) and is configured as alarm P26.20.8 (P_BBCtrlComAlarmEn) = 1
494 | Bosch | OK OK Time | 0 | OK | L/R | The Bosch BLADEcontrol device set Reference algorithm alarm (B_Envr_BBCtrlRefAlgorAlarm) or Lighning Alarm (B_Envr_BBCtrlLightningAlarm) to TRUE and this is configured as warning P26.20.9 (P_BBCtrlDisturbWarningEn) = 1
495 | Bosch |  | 2 | TRIP | L | The Bosch BLADEcontrol device set Reference algorithm alarm (B_Envr_BBCtrlRefAlgorAlarm) or Lighning Alarm
496 | Bosch BLADEcontrol rotor blade dynamic load warning | OK OK Time | 0 | OK | L/R | The Bosch BLADEcontrol device set Imbalance Warning (B_Envr_BBCtrlImbalanceWarning) or dynamic load warning (B_Envr_BBCtrlDynLoadWarning) to TRUE and this is configured as warning P26.20.11 (P_BBCtrlDynLoadWarningEn) = 1
497 | Bosch BLADEcontrol rotor blade dynamic load alarm | AF Down Time | 2 | TRIP | L | The Bosch BLADEcontrol device set Imbalance Warning (B_Envr_BBCtrlImbalanceWarning) or dynamic load warning (B_Envr_BBCtrlDynLoadWarning) to TRUE and this is configured as alarm P26.20.12 (P_BBCtrlDynLoadAlarmEn) = 1
501 | Transformer oil over extreme temperature trip | AF Down Time | 2 | TRIP | A | If transformer oil temperature > P_Envr_TrafoExtremeTemp delay 1 sec, activate SM 501. Restart condition: transformer oil temperature < P_Envr_TrafoExtremeTemp –10°C, delay 1 sec
502 | Transformer oil level too low trip | OK OK Time | 0 | OK | L/R | If transformer oil level protection device reports warning, delay 200ms, activate SM 502.
503 | Transformer gas protection trip | OK OK Time | 0 | OK | L/R | If transformer gas protection device reports alarm, delay 200ms, activate SM 503.
504 | Communication loss for PAIC | AF Down Time | 2 | TRIP | L/R | If controller loses communication to PAIC, delay P_In_DtaAuxSigBoxIOLossTime sec, activate SM 504.
505 | Communication loss for PDIO | AF Down Time | 2 | TRIP | L/R | If controller loses communication to PDIO, delay P_In_DtaAuxSigBoxIOLossTime sec, activate SM 505.
506 | Auxiliary signal box lightning 230V protection indication | OK OK Time | 0 | OK | L/R | If 230V anti-lightning protection fails, activate SM 506.
507 | Auxiliary signal box lightning 690V protection indication | OK OK Time | 0 | OK | L/R | If 690V anti-lightning protection fails, activate SM 507.
508 | Transformer gas alarm | OK OK Time | 0 | OK | L/R | Activate SM 508 if gas protection alarm detected (DI_In_TrafoGasAlarm =1 for 200ms). Reset SM 508 if
509 | Transformer gas release warning | OK OK Time | 0 | OK | A | Set SM 509 if gas pressure release switch open is detected (DI_In_TrafoGasRele =1 lasts 200 ms). ResetSM 509 if DI_In_TrafoGasRele =0 lasts 200 ms.
510 | Transformer_MV SC_Trip | OK OK Time | 2 | OK | L/R | To initiate transformer trip/disconnect from grid, set SCADA command (W_In_MVSCTrip =1) from web page, to trigger MV cabinet switch trips DO_Envr_TrafoCBTrip = 1. Before trigger MV cabinet switch trips DO_Envr_TrafoCBTrip, it should detect Q1 (CB1) status first, controller should disconnect Q1 from grid, set SM 510, and wait pitch angle reach feather position, set DO_Envr_TrafoCBTrip=1.
515 | Wait for Converter to be ready | WOT Weather Out Time | 6.2 | TRIP | A | The converter is not ready for Spinning. The turbine wait in IDLING. (DI_In_CuSpinRdy)
516 | Converter start- up time exceeded | AF Down Time | 2 | TRIP | L/R | The converter is not ready for Spinning takes undefined too long. Further root cause analyzing in Converter (by GE Toolbox) is required. (DI_In_CuSpinRdy)
518 | Brake Procedure Closed Loop Failed to Brake Turbine | AF Down Time | 6.2 | TRIP | L/R | Brake Procedure Closed Loop Failed to Brake Turbine
519 | Rotor lock engaged for long time | AF Down Time | 2 | TRIP | L/R | If the Rotor Lock engaged T1-DI21 = TRUE (DI_In_TbRotorLockEngaged) or the SM319 "Rotor Lock Bridging" is active, for longer then 12h OR after 8 PM then this status message is set. It will be reset automatically, if the Rotor Lock armed T1-DI21 = FALSE (DI_In_TbRotorLockEngaged) and SM319 "Rotor Lock Bridging" = false.
520 | Congurable Stop Auxiliary sensor malfunction | EX External Stop Time | 2 | OK | L/R | Congurable Stop Auxiliary sensor malfunction
521 | Configurable Turbine Stop | EX External Stop Time | 2 | OK | L/R | Configurable Turbine Stop
530 | Voltage Asymmetry Warning from CCU | OK OK Time | 0 | OK | L/R | Voltage Asymmetry Warning from CCU
533 | Under frequency warning from CCU | OK OK Time | 0 | OK | L/R | Under frequency warning from CCU
534 | Over frequency | OK OK Time | 0 | OK | L/R | Over frequency warning from CCU
535 | Fast Disconnect Active from CCU | OK OK Time | 0 | OK | L/R | Fast Disconnect Active from CCU
536 | Fast Blocking Active from CCU | OK OK Time | 0 | OK | L/R | Fast Blocking Active from CCU
538 | CU DTD Parameter update not successful | OK OK Time | 2 | OK | L/R | CU DTD Parameter update not successful
539 | Cu Max Power or Firmware compatibility issue | AF Down Time | 2 | TRIP | L/R | Cu Max Power or Firmware compatibility issue
540 | Turbine Limit Protection Over Voltage | NA Grid Outage Time | 14 | TRIP | L/R | Only for NGG: The Converter is reporting that over voltage protection is active (DI_In_CuOverVoltProtection). The SM must be reset manually.
541 | Turbine Limit Protection Under Voltage | NA Grid Outage Time | 14 | TRIP | L/R | Only for NGG: The Converter is reporting that under voltage protection is active. (DI_In_CuUnderVoltProtection). The SM must be reset manually.
542 | Turbine Limit Protection Voltage Asymmetry | NA Grid Outage Time | 14 | TRIP | L/R | Only for NGG: The Converter is reporting that voltage asymetrie protection is active (DI_In_CuVoltAsymProtection). The SM must be reset manually.
543 | Turbine Limit Protection Over Frequency | NA Grid Outage Time | 14 | TRIP | L/R | Only for NGG: The Converter is reporting that over frequency protection is active (DI_In_CuOverFreqProtection). The SM must be reset manually.
544 | Turbine Limit Protection Under Frequency | NA Grid Outage Time | 14 | TRIP | L/R | Only for NGG: The Converter is reporting that under frequency protection is active (DI_In_CuUnderFreqProtection). The SM must be reset manually.
545 | SubSynchronous Oscillation trip from CCU | OK OK Time | 14 | TRIP | L/R | SubSynchronous Oscillation trip from CCU
546 | SubSynchronous Oscillation warning from CCU | OK OK Time | 0 | OK | L/R | SubSynchronous Oscillation warning from CCU
550 | Turbine connected to WFWM Application | OK OK Time | 0 | OK | A | If P38.20.15 “P_WFWMEnable” = TRUE and SM155 and SM156 are not active and the wake system has no time out (10 min no new package)
551 | Communication between turbine and WFWM Application lost | OK OK Time | 0 | OK | A | If P38.20.15 “P_WFWMEnable” = TRUE and the wake system has a time out (10 min no new package)
552 | WFWM Actively constraining Turbine Operation | OK OK Time | 0 | OK |  | Is set if the WFWM tool curtails a turbine
555 | Generator Idling in speed control | WOT Weather Out Time | 0 | OK | A | The generator winding is not heated up. The Generator stator heater (DO_Gen_TbGenStandbyHeater) is ON and the turbine idle in speed control with P816 rpm (P_GenWarmUpSpeedDemand). Generator heatup end, if Nacelle Temperature (AI_In_TbNacelleTemperature) is + P1025 (P_GenWindingTempOffset) warmer then the lowest of the 3 winding temperature ("U", "V", "W") for more than 5 minutes or if the maximim heatup time P817 (P_GenHeatupTime, default 4h) is exceeded.
601 | Vibration Monitor Timeout | AF Down Time | 2 | TRIP | A | One of teh following disturbance in the communication to the PCH System over Profibus occur * The communication loop with the PCH Firmware is unhelthy (AI_In_uPCH_LoopbackID or AI_In_uPCH_SequenceCounter stop) * The PCH profibus device doesn't exist (DI_In_bPCH_ProfiStatNonExist = 1) * The PCH profibus device doesn't communicate (DI_In_bPCH_ProfiStatNotRdy = 1) * Profibus diagnostics available from PCH Device (DI_In_bPCH_ProfiStatDiag = 1)
602 | SSD Test Failed | AF Down Time | 2 | TRIP | L | The SSD test of the PCH-BOX that was initiated by Turbine PLC failed (Doesn't open and close safety chain). A not successfully passed SSD Test must keep turbine stopped until a SSD Test passed.
800 | Short term particle count limit reached warning | OK OK Time | 0 | OK | A | Warning SM800 “Short term particle count limit reached warning” is generated if the calculated value is equal or larger than P800 “Short term (7 days) particle count limit for warning” and P802 “Short term (7 days) particle count limit for warning” is enabled.
801 | Short term particle count limit reached fault | AF Down Time | 2 | TRIP | A | Fault SM801 “Short term particle count limit reached fault” is generated and turbine is shutdown with BP2 if the calculated value is equal or larger than P801 “Short term (7 days) particle count limit for fault” and P803 “Short term (7 days) particle count limit for fault” is enabled
802 | Long term particle count limit reached warning | OK OK Time | 0 | OK | A | Warning SM802 “Long term particle count limit reached warning” is generated if the resulting value of the subtraction is equal or larger than the limit calculated with P804“Long term (1 year) particle count limit for warning” from the formula above and P806 “Long term (1 year) particle count limit for warning” is enabled.
803 | Long term |  | 2 | TRIP | A | Fault SM803 “Long term particle count limit reached fault” is generated if the resulting value of the subtraction is equal or larger than the limit calculated with P805 “Long term (1 year) particle count limit for fault” from the formula above and P807 “Long term (1 year) particle count limit for fault” is enabled.
804 | Particle rate of change max. samples warning | OK OK Time | 0 | OK | A | If the non-volatile sample counter is equal or greater then the value defined in P809“Rate of change, max. samples for warning” and P811 “Rate of change, max samples warning” is enabled the warning SM804 “Particle rate of change max. samples reached warning” is generated.
805 | Particle rate of change max. samples fault | AF Down | 2 | TRIP | A | If the non-volatile sample counter is equal or above to the value in P810 “Rate of change, max. samples for fault” and P812 “Rate of change, max samples fault” is enabled then the fault SM805 “Particle rate of change max. samples reached fault” is generated and turbine is shutdown with BP2.
806 | Turbine | CST | 14 | TRIP |  | When Eagle ShutDown command is sent from the WebHMI/SCADA and Eagle ShutDown feature is configured (P866 = 1) in the turbine, SM806 will be triggered indicating Eagle ShutDown is active. This will be cleared with Release Eagle ShutDown command from WebHMI/SCADA
807 | Converter | GOT | 14 | TRIP | A | When Phase jump flag (DI_In_CuPhaseJumpActive = true) detected by converter, SM807 is triggered, when the phase jump flag becomes false SM807 resets
808 | Generator stator | OK OK Time | 0 | OK | A | When generator winding 1 temperature crosses P813, this warning is set. This functionality can be enabled by enabling the parameter (P814)
809 | Generator stator | OK OK Time | 0 | OK | A | When generator winding 2 temperature crosses P813, this warning is set. This functionality can be enabled by enabling the parameter (P814)
810 | Generator stator | OK OK Time | 0 | OK | A | When generator winding 3 temperature crosses P813, this warning is set. This functionality can be enabled
814 | Converter Temperature Trip Alarm | AF Down Time | 2 | TRIP | A | If converter sends a temperature warning (DI_In_CuTempWarning = TRUE), sets 814
900 | Rotor over speed threshold in over speed protection function | OK OK Time | 0 | OK |  | If overspeed monitor threshold > 23 OR overspeed monitor threshold < 15 activate SM 900
902 | Cu values received from Cu are frozen for more than 3 seconds | AF Down Time | 6.3 | TRIP | Local | If values (actual torque, grid-monitored real power, actual gen speed) from CCU are unchanged for 3 sec, activate SM902.
903 | Hot weather shutdown initiated | OK OK Time | 2 | TRIP | L/R | If P_outsideAirMaxTemp is set >0 the turbine will trigger SM903 and BP2 whenever the outside temperature crosses the P_outsideAirmaxTemp for 60 secs, even if P_CurtPowerDerateOutTempEn is set to false. In this case the turbine should not curtail even if temperature P938 is crossed.
906 | WindInertia Event is Active. | OK OK Time | 0 | OK |  | If DeadBand Out < P51.3 (P_DynCtlDeadbandLoSPWInertia) AND SPWR > 0 for 50 sec AND WindIntertia feature enabled.
907 | Yaw Brake 230Volt not OK | AF Down Time | 2 | TRIP | A | Yaw control circuit will monitor voltage signal just prior to yaw brake activation. SM 907 generated when voltage is too low
908 | AEPA1 accelerometer failure | OK OK Time | 0 | OK | L/R | Sensor1 error delay for 250 ms then SM 908 generated.
909 | AEPA2 accelerometer failure | OK OK Time | 0 | OK | L/R | Sensor2 error delay for 250 ms then SM 909 generated.
910 | AEPA3 accelerometer failure | OK OK Time | 0 | OK | L/R | Sensor3 error delay for 250 ms then SM 910 generated.
911 | 1P High Imbalance detected | Down Time | 2 | TRIP | A | High Imbalance detected. It is auto resettable three times.
914 | High Turbulence Speed Limit Active | OK OK Time | 0 | OK |  | High Turbulence Speed Limit Active
916 | Grid Monitor opens safety chain | AF Down Time | 6.3 | TRIP | L | The Grid Monitoring in the CCU opens the safety chain (DI_In_CuGridMonSafetyChainOK - 1=OK, 0=Safety chain open)
919 | CCU delta torque | OK OK Time | 0 | OK | A | The turbine is torque curtailed by the Converter (DI_In_CuTorqueReducedActive = 1,
920 | CCU delta speed curtailment is active | OK OK Time | 0 | OK | A | The turbine is speed curtailed by the Converter (DI_In_CuSpeedReducedActive = 1, AI_In_CuDeltaSpeedReq)
999 | Generator OverSpeed during Torque Loss | AF Down Time | 6.11, 6.15 | TRIP | L/R | Generator OverSpeed during Torque Loss
1000 | Pitch Bearing Rotate Function ongoing | OK OK Time | 0 | OK |  | Pitch Bearing Rotate Function ongoing
1001 | Pitch Bearing Rotate Function too long | AF Down Time | 2 | TRIP | L | Pitch Bearing Rotate Function too long
1002 | Pitch Bearing Rotate Function paused | OK OK Time | 0 | OK |  | Pitch Bearing Rotate Function paused
1003 | Pitch Bearing Rotate Function complete | OK OK Time | 0 | OK |  | Pitch Bearing Rotate Function complete
1004 | Pitch Bearing Rotate Function aborted due to extended pause | OK OK Time | 0 | OK |  | Pitch Bearing Rotate Function aborted due to extended pause
1005 | Pitch Bearing Rotate Function aborted | OK OK Time | 2 | TRIP |  | BRF Aborted
1006 | Severe Blade Problems indicating pitch runaway condition in axis 1 | AF Down Time | 14 | TRIP | L/R | Severe Blade Problems indicating pitch runaway condition in axis 1, it will be triggered if SM145 (Pitch control deviation axis 1) is set and blade 1 is moving to feather with a higher rate than P1364 or to power with a lower rate than P1363
1007 | Severe Blade Problems indicating pitch runaway condition in axis 2 | AF Down Time | 14 | TRIP | L/R | Severe Blade Problems indicating pitch runaway condition in axis 2, it will be triggered if SM145 (Pitch control deviation axis 2) is set and blade 1 is moving to feather with a higher rate than P1364 or to power with a lower rate than P1363
1008 | Severe Blade Problems indicating pitch runaway condition in axis 3 | AF Down Time | 14 | TRIP | L/R | Severe Blade Problems indicating pitch runaway condition in axis 3, it will be triggered if SM145 (Pitch control deviation axis 3) is set and blade 1 is moving to feather with a higher rate than P1364 or to power with a lower rate than P1363
1016 | Pitch Communication short term fault axis 1 | OK OK Time | 0 | OK | A | The Pitch WEPA Card axis 1 Link-OK signal goes false WEPA-H1-LINK_OK_WEPA_R (DI_In_CommunAEPA1_Ok)
1017 | Pitch Communication short term fault axis 2 | OK OK Time | 0 | OK | A | The Pitch WEPA Card axis 2 Link-OK signal goes false WEPA-H2-LINK_OK_WEPA_R (DI_In_CommunAEPA2_Ok)
1018 | Pitch Communication short term fault axis 3 | OK OK Time | 0 | OK | A | The Pitch WEPA Card axis 3 Link-OK signal goes false WEPA-H3-LINK_OK_WEPA_R (DI_In_CommunAEPA3_Ok)
1050 | Pitch axis 1 speed loss detected | AF Down Time | 14 | TRIP | L/R | Possible loss of incremental encoder, motor volts without speed feedback from encoder or K21 not closing
1051 | Pitch axis 2 speed loss detected | AF Down Time | 14 | TRIP | L/R | Possible loss of incremental encoder, motor volts without speed feedback from encoder or K21 not closing
1052 | Pitch axis 3 speed loss detected | AF Down Time | 14 | TRIP | L/R | Possible loss of incremental encoder, motor volts without speed feedback from encoder or K21 not closing
1053 | Pitch axis 1 missing marker pulses detected | AF Down Time | 14 | TRIP | L/R | Missing marker pulses from the incremental encoder detected
1054 | Pitch axis 2 missing marker pulses detected | AF Down Time | 14 | TRIP | L/R | Missing marker pulses from the incremental encoder detected
1055 | Pitch axis 3 missing marker pulses detected | AF Down Time | 14 | TRIP | L/R | Missing marker pulses from the incremental encoder detected
1056 | Pitch axis 1 missing pulses detected | AF Down Time | 14 | TRIP | L/R | Incremental encoder missed more than 50 pulses at the receipt of marker pulse
1057 | Pitch axis 2 missing pulses detected | AF Down Time | 14 | TRIP | L/R | Incremental encoder missed more than 50 pulses at the receipt of marker pulse
1058 | Pitch axis 3 missing pulses detected | AF Down Time | 14 | TRIP | L/R | Incremental encoder missed more than 50 pulses at the receipt of marker pulse
1059 | Pitch axis 1 wrong angle at limit switch detected | AF Down Time | 14 | TRIP | L/R | Blade angle error too big at drop out of 89 deg limit switch.
1060 | Pitch axis 2 wrong angle at limit switch detected | AF Down Time | 14 | TRIP | L/R | Blade angle error too big at drop out of 89 deg limit switch.
1061 | Pitch axis 3 wrong angle at limit switch detected | AF Down Time | 14 | TRIP | L/R | Blade angle error too big at drop out of 89 deg limit switch.
1062 | Pitch axis 1 low DC link voltage detected | AF Down Time | 14 | TRIP | L/R | DC Link voltage of pitch converter is less than lower limit
1063 | Pitch axis 2 low DC link voltage detected | AF Down Time | 14 | TRIP | L/R | DC Link voltage of pitch converter is less than lower limit
1064 | Pitch axis 3 low DC link voltage detected | AF Down Time | 14 | TRIP | L/R | DC Link voltage of pitch converter is less than lower limit
1065 | Pitch axis 1 motor brake fault | AF Down Time | 14 | TRIP | L/R | Motor brake current and voltage not OK
1066 | Pitch axis 2 motor brake fault | AF Down Time | 14 | TRIP | L/R | Motor brake current and voltage not OK
1067 | Pitch axis 3 motor brake fault | AF Down Time | 14 | TRIP | L/R | Motor brake current and voltage not OK
1068 | Pitch axis 1 flux not OK | AF Down Time | 14 | TRIP | L/R | Motor magnetic field flux not OK
1069 | Pitch axis 2 flux not OK | AF Down Time | 14 | TRIP | L/R | Motor magnetic field flux not OK
1070 | Pitch axis 3 flux not OK | AF Down Time | 14 | TRIP | L/R | Motor magnetic field flux not OK
1071 | Pitch axis 1 over speed detected | AF Down Time | 14 | TRIP | L/R | Motor over speed - speed feedback has exceeded the max. allowed speed
1072 | Pitch axis 2 over speed detected | AF Down Time | 14 | TRIP | L/R | Motor over speed - speed feedback has exceeded the max. allowed speed
1073 | Pitch axis 3 over speed detected | AF Down Time | 14 | TRIP | L/R | Motor over speed - speed feedback has exceeded the max. allowed speed
1074 | Pitch axis 1 safety relay dropped | AF Down Time | 14 | TRIP | L/R | Safety relay PLC signal set to FALSE
1075 | Pitch axis 2 safety relay dropped | AF Down Time | 14 | TRIP | L/R | Safety relay PLC signal set to FALSE
1076 | Pitch axis 3 safety relay dropped | AF Down Time | 14 | TRIP | L/R | Safety relay PLC signal set to FALSE
1077 | Pitch axis 1 PIC communication not OK | AF Down Time | 14 | TRIP | L/R | Internal PIC (microcontroller) to FPGA communications not OK
1078 | Pitch axis 2 PIC communication not OK | AF Down Time | 14 | TRIP | L/R | Internal PIC (microcontroller) to FPGA communications not OK
1079 | Pitch axis 3 PIC communication not OK | AF Down Time | 14 | TRIP | L/R | Internal PIC (microcontroller) to FPGA communications not OK
1080 | Pitch axis 1 phase loss detected | AF Down Time | 14 | TRIP | L/R | Phase from main supply is missing. Check fuses.
1081 | Pitch axis 2 phase loss detected | AF Down Time | 14 | TRIP | L/R | Phase from main supply is missing. Check fuses.
1082 | Pitch axis 3 | AF Down | 14 | TRIP | L/R | Phase from main supply is missing.
1201 | Blown Fuses | AF Down | 14 | TRIP | A | Either
1202 | Contactor or | AF Down | 14 | TRIP | A | Either
1203 | Cooling system | AF Down | 14 | TRIP | A | Either
1204 | Code sequencing | AF Down | 14 | TRIP | A | Either
1205 | DC Link over- voltage | AF Down | 14 | TRIP | A | Either
1206 | DTA Fan | AF Down | 14 | TRIP | A | Either
1207 | DTA wiring | AF Down | 14 | TRIP | A | Either
1208 | IGBT damage | AF Down | 14 | TRIP | A | Either
1209 | HSSL / HSLA, Line converter | AF Down | 14 | TRIP | A | Either
1210 | HSSL / HSLA, | AF Down | 14 | TRIP | A | Either
1211 | Invalid PWA , line bridge board | AF Down | 14 | TRIP | A | Either
1212 | Invalid PWA, rotor bridge board | AF Down | 14 | TRIP | A | Either
1213 | Voltage offset, | AF Down | 14 | TRIP | A | Either
1214 | Voltage offset, | AF Down | 14 | TRIP | A | Either
1215 | Voltage offset, | AF Down | 14 | TRIP | A | Either
1216 | Voltage offset, | AF Down | 14 | TRIP | A | Either
1217 | Reverse Power | AF Down | 14 | TRIP | A | Either
1218 | Power Supply | AF Down | 14 | TRIP | A | Either
1219 | Current offset, | AF Down | 14 | TRIP | A | Either
1220 | Current offset, | AF Down | 14 | TRIP | A | Either
1221 | Current offset, | AF Down | 14 | TRIP | A | Either
1222 | Current offset, | AF Down | 14 | TRIP | A | Either
1223 | Wiring Issue, | AF Down | 14 | TRIP | A | Either
1224 | Wiring Issue, Grid or Line converter | AF Down | 14 | TRIP | A | Either
1225 | Generator I/O | AF Down | 14 | TRIP | A | Either
1226 | Grid frequency | AF Down | 14 | TRIP | A | Either
1227 | Rotor AEBI | AF Down | 14 | TRIP | A | Either
1228 | Tachometer | AF Down | 14 | TRIP | A | Either
1229 | Thermistor failure | AF Down | 14 | TRIP | A | Either
1230 | Dynamic-Brake | AF Down | 14 | TRIP | A | Either
1231 | C to C | AF Down | 14 | TRIP | A | Either
1232 | Converter stat | AF Down | 14 | TRIP | A | Either
1233 | DC Link under- voltage | AF Down | 14 | TRIP | A | Either
1234 | Drive Train | AF Down | 14 | TRIP | A | Either
1235 | DTA over- | AF Down | 14 | TRIP | A | Either
1236 | DTA Pump | AF Down | 14 | TRIP | A | Either
1237 | Grid - 690 single phase open | AF Down | 14 | TRIP | A | Either
1238 | Grid - 690 three phase open | AF Down | 14 | TRIP | A | Either
1239 | Grid Single phase open | AF Down | 14 | TRIP | A | Either
1240 | Grid three phase open | AF Down | 14 | TRIP | A | Either
1241 | Grid Islanding | AF Down | 14 | TRIP | A | Either
1242 | Grid Loss | AF Down | 14 | TRIP | A | Either
1243 | Grid Overvoltage | AF Down | 14 | TRIP | A | Either
1244 | Grid Transient | AF Down | 14 | TRIP | A | Either
1245 | Grid | AF Down | 14 | TRIP | A | Either
1246 | Grid voltage | AF Down | 14 | TRIP | A | Either
1247 | Grid Fast | AF Down | 14 | TRIP | A | Either
1248 | Grid Fast | AF Down | 14 | TRIP | A | Either
1249 | Synchronization | AF Down | 14 | TRIP | A | Either
1250 | Ground Fault, | AF Down | 14 | TRIP | A | Either
1251 | Ground Fault, | AF Down | 14 | TRIP | A | Either
1252 | Ground Fault, | AF Down | 14 | TRIP | A | Either
1253 | Ground Fault, | AF Down | 14 | TRIP | A | Either
1254 | DTA under- | AF Down | 14 | TRIP | A | Either
1255 | Thermal Turbine | AF Down | 14 | TRIP | A | Either
1256 | IGBT or Diode Junction Over- temperature , DB circuit | AF Down | 14 | TRIP | A | Either
1257 | IGBT or Diode Junction Over- temperature, Line Converter | AF Down | 14 | TRIP | A | Either
1258 | IGBT or Diode Junction Over- temperature, Rotor Converter | AF Down | 14 | TRIP | A | Either
1259 | IGBT or Diode Junction Under- temperature, Line Converter | AF Down | 14 | TRIP | A | Either
1260 | IGBT or Diode Junction Under- temperature, | AF Down | 14 | TRIP | A | Either
1261 | IOC, Line | AF Down | 14 | TRIP | A | Either
1262 | IOC, Rotor | AF Down | 14 | TRIP | A | Either
1263 | IOC, DB IGBT | AF Down | 14 | TRIP | A | Either
1264 | Timed Over- | AF Down | 14 | TRIP | A | Either
1265 | Timed Over- | AF Down | 14 | TRIP | A | Either
1266 | Regulator | AF Down | 14 | TRIP | A | Either
1267 | Regulator | AF Down | 14 | TRIP | A | Either
1268 | Torque | AF Down | 14 | TRIP | A | Either
1269 | Cell Test Failure manual, Line converter | AF Down | 14 | TRIP | A | Either
1270 | Cell Test Failure manual, Rotor converter | AF Down | 14 | TRIP | A | Either
1271 | Cell Test Failure at startup, Line converter | AF Down | 14 | TRIP | A | Either
1272 | Cell Test Failure at startup, Rotor converter | AF Down | 14 | TRIP | A | Either
1273 | Toolbox | AF Down | 14 | TRIP | A | Either
1274 | Mis-configuration | AF Down | 14 | TRIP | A | Either
1275 | Invalid Generator | AF Down | 14 | TRIP | A | Either
1276 | Firmware | AF Down | 14 | TRIP | A | Either
1277 | MarkStat Process | AF Down | 14 | TRIP | A | Either
1278 | Invalid PWA, Line I/O board | AF Down | 14 | TRIP | A | Either
1279 | Invalid PWA, | AF Down | 14 | TRIP | A | Either
1280 | Invalid HSLA, Line or Rotor board | AF Down | 14 | TRIP | A | Either
1281 | Invalid REFB | AF Down | 14 | TRIP | A | Either
1282 | Grid Distortion | AF Down | 14 | TRIP | A | Either
1283 | Rotor timed over- voltage | AF Down | 14 | TRIP | A | Either
1284 | Invalid WEMA Pic Version | AF Down | 14 | TRIP | A | Either
1285 | Grid voltage or frequency out of tolerance | AF Down | 14 | TRIP | A | Either
1286 | Improper turbine | AF Down | 14 | TRIP | A | Either
1287 | Safety Chain Trip | AF Down | 14 | TRIP | A | Either
1288 | Overspeed | AF Down | 14 | TRIP | A | Either
1289 | Underspeed | AF Down | 14 | TRIP | A | Either
1290 | IGBT Desat, Line Bridge | AF Down | 14 | TRIP | A | Either
1291 | IGBT Desat, Rotor Bridge | AF Down | 14 | TRIP | A | Either
1292 | Gate Drive Power Supply undervoltage, Line AEDB or AEBI | AF Down | 14 | TRIP | A | Either
1293 | Gate Drive Power Supply undervoltage, RotorAEBI | AF Down | 14 | TRIP | A | Either
1294 | REBF Control | AF Down | 14 | TRIP | A | Either
1295 | REBF Control | AF Down | 14 | TRIP | A | Either
1296 | I/O board Gain or Offset out of tolerance, line | AF Down | 14 | TRIP | A | Either
1297 | I/O board Gain or Offset out of tolerance, rotor | AF Down | 14 | TRIP | A | Either
2771 | High generator | OK OK Time | - | OK | A/L/R | Message is set if there is an active power limitation because of a high generator winding temperature
2772 | High gearbox | OK OK Time | - | OK | A/L/R | Message is set if there is an active power limitation because of a high gearbox temperature
2773 | High outside | OK OK Time | - | OK | A/L/R | Message is set if there is an active power limitation because of a high ambient temperature